## Cover
Colours Legend |  | Over 1 year count since reading |  |  | Data updated | 2024-05-08
Multiple Single Systems |  | 122
True A & B Systems
True A & B Systems
BRAG <0 = BLACK 0 - 10 = RED 10 - 25 = AMBER >25 = GREEN | Region | Reading Date | Space | % Power Remaining (@ 80% of N ) | kW Power Remaining (@ 80% of N ) | % Power Remaining (Inc. Full Batt Recharge) | kW Power Remaining (Inc. Full Batt Recharge) | % Autonomy Remaining | kW Autonomy Remaining | % Cooling Remaining (@ 75% of N) | kW Cooling Remaining (@ 75% of N) | P-Core | RA | PX | Amitie | Op-EX | Total Allocated Load kW | Comments
ABH;DC SYS01 | ANGLIA | 2024-05-02 |  | 70.9699 | 4.53 | -14.2473 | -0.23108 | 85.9135 | 11.3014 | 75.2933 | 5.647 | 0 | 0 | 0 | 0 | 0 | 0
ABN;DC SYS01 | SCOTLAND | 2022-01-13 11:00 |  | -8.422 | -1.377 | -371.4001 | -13.9665 | 32.1179 | 8.3874 | 21.2133 | 4.773 | 0 | 0 | 0 | 0 | 0 | 6.5
ABNTB1;DC SYS01 | SCOTLAND | 2024-05-02 |  | 40.4238 | 15.2983 | 18.5635 | 5.1395 | 28.8467 | 9.1407 | 33.1956 | 11.2035 | 0 | 0 | 0 | 0 | 0 | 2
ABNTD1;DCSYS01 | SCOTLAND | 2024-05-02 |  | 34.4401 | 7.6941 | -6.4751 | -0.8907 | 35.9094 | 8.2063 | 67.4522 | 30.3535 | 0 | 0 | 0 | 0 | 0 | 5
ACTN01;DC SYS01a | LONDON | 2024-05-02 |  | 49.9463 | 47.0243 | 25.4193 | 16.0618 | 46.9809 | 41.7585 | 82.8934 | 464.4105 | 0 | RA | 0 | 0 | OPEX | 6.85
ACTN01;DC SYS01b | LONDON | 2024-05-02 |  | 48.2591 | 45.4358 | 22.9054 | 14.4733 | 45.1937 | 40.17 | [7 empty] | 5.55
ANSTW1; DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | 2021-10-14 12:10 |  | 61.6677 | 1.7746 | 67.8739 | 2.3304 | 57.4441 | 1.4889 | 78.0488 | 3.922 | 0 | 0 | 0 | 0 | 0 | 0.4
ASH;DC SYS01 | SOUTH EAST | 2022-05-10 12:00 |  | 50.2688 | 8.8239 | 44.0927 | 6.8847 | 30.9156 | 3.9065 | 10.4667 | 1.0205 | 0 | 0 | 0 | 0 | 0 | 0.5
ASMN02;DC SYS01 | THAMES VALLEY | 2022-01-18 15:00 |  | 66.6667 | 10.9 | 60.9375 | 8.502 | 46.0866 | 4.6588 | 95.1556 | 107.05 | 0 | 0 | 0 | 0 | 0 | 0
AYRN01; DC SYS01 | SCOTLAND | 2013-11-07 |  | 86.413 | 3.4662 | 88.6364 | 4.251 | 84.2303 | 2.911 | 96.3667 | 14.455 | 0 | 0 | 0 | 0 | 0 | 0
AZTCD1&2;DC SYS01 | SOUTH WEST | 2023-02-15 |  | 42.9468 | 40.4343 | -2.7314 | -1.4282 | 49.6389 | 52.9453 | 53.7931 | 62.5345 | 0 | RA | 0 | 0 | 0 | 6.9
BCT;DC SYS01 | MIDLANDS | 2024-05-02 |  | 39.0808 | 4.9891 | -24.8445 | -1.5476 | 48.7114 | 7.3862 | 71.1963 | 19.223 | 0 | 0 | 0 | 0 | 0 | 2
BDEN02;DC SYS01 | SOUTH WEST | 2023-03-02 |  | 36.9318 | 3.5425 | -7.3916 | -0.41638 | 54.0116 | 7.1049 | 73.1133 | 16.4505 | 0 | 0 | 0 | 0 | 0 | 0
BDEN06;DC SYS01 | SOUTH WEST | 2023-05-02 |  | 16.5392 | 6.49 | 7.6506 | 2.7132 | -17.8091 | -4.9508 | 61.8365 | 53.065 | 0 | 0 | 0 | 0 | 0 | 5.5
BDFN02;DC SYS01a | NORTHERN HOME COUNTIES | 2024-05-02 |  | 48.898 | 56.9615 | 25.7864 | 20.6841 | 44.1885 | 47.1318 | 16.2462 | 26.197 | P-Core | RA | PX | 0 | OPEX | 12.55
BDFN02;DC SYS01b | NORTHERN HOME COUNTIES | 2024-05-02 |  | 35.1672 | 40.9665 | 5.8458 | 4.6891 | 29.1924 | 31.1368 |  |  | 0 | 0 | 0 | 0 | 0 | 11.65
BFDTB1;DC SYS01 | NORTH EAST | 2022-02-08 14:30 |  | 54 | 4.7088 | 47.4286 | 3.6188 | 23.2629 | 1.216 | 89.3035 | 33.4888 | 0 | 0 | 0 | 0 | 0 | 0
BFEC01;DC SYS01 | NORTHERN IRELAND | 2023-03-15 |  | 17.539 | 6.997 | -1.4478 | -0.4695 | -16.9746 | -4.7738 | 39.0796 | 21.103 | 0 | RA | 0 | 0 | 0 | 18.4
BFTN03;DC SYS01 | NORTHERN IRELAND | 2023-03-15 |  | -3.5335 | -1.3533 | -82.6181 | -17.9387 | 6.0052 | 2.5333 | 43.152 | 30.0985 | 0 | RA | 0 | 0 | 0 | 14.2
BHM;DC SYS02 | MIDLANDS | 2023-02-07 |  | 53.8934 | 25.8003 | 41.9771 | 15.9685 | 37.9177 | 13.4811 | -133.5714 | -12.6225 | P-Core | 0 | 0 | 0 | 0 | 0
BHMN05;DC SYS A | MIDLANDS | 2024-05-02 |  | 63.6477 | 58.9086 | 60.2429 | 50.9821 | 30.0053 | 14.4231 | 59.2176 | 48.8545 | 0 | 0 | 0 | 0 | 0 | 1
BHMN05;DC SYS B | MIDLANDS | 2024-05-02 |  | 59.0547 | 54.6576 | 54.3375 | 45.0961 | 28.9402 | 15.4339 | 54.0648 | 44.6035 | 0 | 0 | 0 | 0 | 0 | 1
BHMN08;DCSYS03A | MIDLANDS | 2022-07-12 |  | 65.1303 | 24.9437 | 48.78 | 12.7183 | 62.4384 | 22.1991 | 70.3233 | 31.6455 | 0 | RA | PX | 0 | OPEX | 7.85
BHMN08;DCSYS03B | MIDLANDS | 2022-07-12 |  | 58.7422 | 22.4972 | 39.3966 | 10.2718 | 55.5572 | 19.7526 | 64.8867 | 29.199 | 0 | 0 | 0 | 0 | 0 | 8.28
BHMTF1;DC SYS A | MIDLANDS | 2024-05-02 |  | 80.8693 | 32.262 | 72.8084 | 20.4355 | 78.5338 | 27.9216 | 91.52 | 82.368 | 0 | RA | 0 | 0 | 0 | 2.4
BHMTF1;DC SYS B | MIDLANDS | 2024-05-02 |  | 75.9689 | 29.0947 | 64.7008 | 16.8693 | 74.1137 | 26.3501 | 89.7739 | 80.7965 | 0 | 0 | 0 | 0 | 0 | 2.5
BHWCN1;DC SYS01 | LONDON | 2021-08-25 13:30 |  | 39.6737 | 7.611 | 18.7959 | 2.6787 | 23.6771 | 3.5902 | 22.8467 | 3.427 | 0 | 0 | 0 | 0 | 0 | 1
BIFTS1; DC SYS01 | NORTH WEST | 2024-03-05 |  | 57.6087 | 2.8885 | 64.5455 | 3.8695 | 50.7986 | 2.1945 | 43.32 | 1.6245 | 0 | 0 | 0 | 0 | 0 | 0
BKBN41;DC SYS01 | NORTH WEST | 2024-05-02 |  | 50.8855 | 6.4961 | 33.8056 | 3.2021 | 37.9748 | 3.8388 | 72.1333 | 16.23 | 0 | 0 | 0 | 0 | 0 | 3
BKLN05;DC SYS02 | THAMES VALLEY | 2024-05-03 |  | -5.2526 | -5.0291 | -15.857 | -13.7927 | -88.963 | -47.4444 | 22.6398 | 93.6155 | P-Core | 0 | 0 | 0 | 0 | 37.8
BKLN05;DC SYS03;NEAR CK | THAMES VALLEY | 2024-05-03 |  | 6.0292 | 5.3878 | -81.3584 | -37.6715 | 21.2693 | 22.6861 |  |  | P-Core | 0 | 0 | 0 | 0 | 21
BKLN05;DC SYS04a | THAMES VALLEY | 2024-05-02 |  | 44.2047 | 107.063 | 21.4092 | 36.8125 | 36.652 | 78.1866 |  |  | P-Core | RA | PX |  | OPEX | 62.65
BKLN05;DC SYS04b | THAMES VALLEY | 2024-05-02 |  | 50.3029 | 121.8325 | 29.9987 | 51.582 | 43.5756 | 92.9561 | 67.5783 | 250.8845 | 0 | 0 | 0 | 0 | 0 | 62.65
BMGV03; DC SYS A | MIDLANDS | 2021-10-29 10:00 |  | 82.0312 | 28.6125 | 76.0417 | 19.8925 | 77.7141 | 21.8557 | 71.0141 | 47.9345 | 0 | 0 | 0 | 0 | 0 | 0
BMGV03; DC SYS B | MIDLANDS | 2021-10-29 12:00 |  | 61.875 | 21.582 | 49.1667 | 12.862 | 52.7152 | 14.8252 |  |  | 0 | 0 | 0 | 0 | 0 | 0
BMTDN1;DC SYS01 | SOUTH | 2022-11-14 |  | 26.6609 | 2.2621 | 32.3131 | 2.9706 | -113.3916 | -3.3065 | 44.6889 | 5.0275 | 0 | 0 | 0 | 0 | 0 | 0.5
BPL;DC SYS01 | NORTH WEST | 2024-05-02 |  | -2.5154 | -0.2007 | -32.8164 | -2.021 | -30.3548 | -1.9047 | -36.325 | -2.1795 | 0 | 0 | 0 | 0 | 0 | 5.4
BRETS1;DC SYS01 | SCOTLAND | 2021-12-08 13:10 |  | 76.7202 | 2.007 | 74.6038 | 1.789 | 68.8115 | 1.3436 | 87.8806 | 4.416 | 0 | 0 | 0 | 0 | 0 | 0.5
BRRTS1; DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | 2024-05-02 |  | 30.5347 | 0.48726 | 1068.5438 | -1.223 | 73.6823 | 3.1035 | 70.44 | 2.6415 | 0 | 0 | 0 | 0 | 0 | 0.4
BSG;DC SYS01 | THAMES VALLEY | 2023-06-14 |  | 38.4572 | 12.2737 | 12.5256 | 2.8125 | 30.1591 | 8.4817 | 40.4803 | 13.3585 | 0 | 0 | 0 | 0 | 0 | 4
BSH;DC SYS01;GND | MIDLANDS | 2024-03-05 |  | 40.2849 | 35.3568 | -18.2843 | -8.1015 | 50.8629 | 54.2508 | 48.237 | 48.84 | P-Core | RA | PX | 0 | 0 | 20.8
BSH;DC SYS02;GND | MIDLANDS | 2024-04-02 |  | 2.973 | 2.6093 | -92.1922 | -40.849 | 20.1605 | 21.5033 | 15.8938 | 16.0925 | P-Core | 0 | 0 | 0 | 0 | 23.3
BSH;DC SYS03;GND | MIDLANDS | 2024-05-02 |  | 45.7864 | 40.1853 | 28.0251 | 18.527 | 33.0848 | 23.5257 | 53.0059 | 53.6685 | P-Core | 0 | 0 | 0 | 0 | 3.6
BSHN03;DC SYS A | MIDLANDS | 2024-05-02 |  | 58.0829 | 121.176 | 55.9784 | 111.2025 | 9.0363 | 8.6873 | 56.0975 | 227.195 | 0 | 0 | 0 | 0 | 0 | 16.6
BSHN03;DC SYS B | MIDLANDS | 2024-05-02 |  | 56.6904 | 118.271 | 54.5161 | 108.2975 | 6.0146 | 5.7823 |  |  | 0 | 0 | 0 | 0 | 0 | 14.6
BTFTB1;DC SYS01 | LONDON | 2024-05-02 |  | 19.9375 | 16.544 | -10.4967 | -6.3111 | 5.5079 | 3.8725 | 52.376 | 73.0645 | P-Core | 0 | 0 | 0 | 0 | 0
BTFTB1;DC SYS02 | LONDON | 2024-05-02 |  | 31.6705 | 30.3231 | -0.36897 | -0.2405 | 26.3956 | 23.4615 | 53.1022 | 74.0775 | 0 | RA | PX | 0 | OPEX | 32.45
BTLCD1;DC SYS01 | SOUTH WEST | 2023-03-02 |  | 35.9347 | 24.128 | 12.3017 | 6.034 | 23.5222 | 13.2304 | 50.9789 | 44.734 | 0 | 0 | 0 | 0 | 0 | 2.25
BTLN08;DC SYS01 | SOUTH WEST | 2023-03-16 |  | 1.5759 | 1.0059 | -73.6059 | -26.6365 | 11.6482 | 8.2827 | 33.519 | 31.6755 | P-Core | 0 | 0 | 0 | 0 | 5
BTLN09;DC SYS01 | SOUTH WEST | 2024-05-03 |  | 9.5803 | 8.4083 | -43.7433 | -24.15 | 10.7168 | 9.5255 | 25.485 | 27.1415 | 0 | RA | PX | AM | OPEX | 48.13
BTN-DCSYS01 | SOUTH | 2021-10-22 16:30 |  | 57.5712 | 29.3983 | 36.6165 | 12.5164 | 52.8639 | 24.2988 | 63.89 | 38.334 | 0 | RA | 0 | 0 | 0 | 2.7
BTNW01;DC SYS01 | MIDLANDS | 2024-05-02 |  | 63.4075 | 7.0828 | 51.9846 | 4.4254 | 54.4009 | 4.8765 | 40.7609 | 2.8125 | 0 | 0 | 0 | 0 | 0 | 0
BTRTP1;DC SYS01 | SCOTLAND | 2024-05-02 |  | 72.6776 | 20.8757 | 57.497 | 10.6166 | 72.0942 | 20.2752 | 91.28 | 82.152 | 0 | 0 | 0 | 0 | 0 | 0
BYR;DC SYS01 | NORTHERN IRELAND | 2022-11-08 |  | 91.6667 | 2.9975 | 85.7143 | 1.635 | 92.4002 | 3.3131 | 97.5778 | 10.9775 | 0 | 0 | 0 | 0 | 0 | 0
CAMN02;DC SYS01 | ANGLIA | 2022-05-05 13:00 |  | 47.2171 | 7.72 | 19.4155 | 2.0793 | 43.0859 | 6.5332 | 61.6444 | 13.87 | 0 | 0 | 0 | 0 | 0 | 1
CAMN41;DC SYS01 | ANGLIA | 2022-02-04 13:00 |  | 70.543 | 9.0056 | 60.2992 | 5.7116 | 62.7997 | 6.3483 | 66.5733 | 7.4895 | 0 | 0 | 0 | 0 | 0 | 0
CBY;DC SYS01 | SOUTH EAST | 2021-09-09 17:00 |  | 63.3224 | 14.1466 | 41.5895 | 5.8343 | 62.4404 | 13.622 | 51.443 | 8.681 | 0 | 0 | 0 | 0 | 0 | 1
CDFN02;DC SYS01 | WALES | 2024-05-02 |  | 50.6035 | 20.9953 | 31.8263 | 9.5677 | 42.356 | 15.0591 | 8.9133 | 2.0055 | 0 | 0 | 0 | 0 | 0 | 3
CELL01;DC SYS01 | MIDLANDS | 2021-11-01 11:00 |  | 66.7008 | 4.2575 | 52.6699 | 2.3653 | 72.7868 | 5.6851 | 64.575 | 3.8745 | 0 | 0 | 0 | 0 | 0 | 0
CFDTN1;DC SYS01 | ANGLIA | 2023-05-12 |  | 43.6423 | 10.4464 | -4850.4587 | -13.2175 | 70.6515 | 32.4748 | 18.2424 | 3.01 | 0 | 0 | 0 | 0 | 0 | 1.5
CHDCD1;DC SYS01 | NORTH EAST | 2024-05-02 |  | 73.3607 | 11.7066 | 70.4545 | 10.137 | 51.2858 | 4.4754 | 29.15 | 1.749 | 0 | 0 | 0 | 0 | 0 | 0
CHMN21;DC SYS01 | SOUTH WEST | 2024-05-02 |  | 76.6621 | 7.3401 | 59.2445 | 3.2482 | 77.8955 | 7.8743 | 80.1378 | 9.0155 | 0 | 0 | 0 | 0 | 0 | 0
CHTN07;DC SYS01 | LONDON | 2023-10-12 |  | 34.2961 | 30.28 | 25.305 | 19.6525 | -8.7747 | -4.6796 | 11.5306 | 20.755 | P-Core | 0 | 0 | 0 | 0 | 15.5
CHTN07;DC SYS02 | LONDON | 2023-10-12 |  | 20.3464 | 25.859 | -8.3104 | -7.7675 | 5.087 | 5.4258 |  |  | P-Core | 0 | 0 | 0 | 0 | 1.5
CHTTN3;DC SYS01A | LONDON | 2022-08-31 |  | 60.8032 | 36.8704 | 44.8509 | 19.3301 | 55.4316 | 29.5619 | 75.7802 | 148.908 | 0 | RA | PX | 0 | OPEX | 7.8
CHTTN3;DC SYS01B | LONDON | 2023-02-22 |  | 60.7125 | 36.8154 | 44.7233 | 19.2751 | 55.3285 | 29.5069 |  |  | 0 | 0 | 0 | 0 | 0 | 8.4
CKNN03-DCSYS01a | SOUTH WEST | 2024-05-02 |  | 67.5334 | 18.3204 | 61.3569 | 13.9844 | 49.4101 | 8.6021 | 92.1711 | 103.6925 | 0 | 0 | 0 | AM | 0 | 6.9
CKNN03-DCSYS01b | SOUTH WEST | 2024-05-02 |  | 64.085 | 17.3849 | 57.2524 | 13.0489 | 44.0366 | 7.6666 | 91.3396 | 102.757 | 0 | 0 | 0 | 0 | 0 | 6.8
COV;DC SYS01a | MIDLANDS | 2023-10-24 |  | 51.6984 | 27.274 | 23.3509 | 7.763 | 52.2186 | 27.8484 | 43.1311 | 38.818 | 0 | 0 | 0 | 0 | OPEX | 9.35
COV;DC SYS01b | MIDLANDS | 2023-10-24 |  | 51.2852 | 27.056 | 22.6951 | 7.545 | 51.8098 | 27.6304 | [7 empty] | 9.35
COWL02;DC SYS01 | THAMES VALLEY | 2024-05-02 |  | 69.5238 | 7.957 | 63.5328 | 6.0767 | 61.0888 | 5.476 | 66.781 | 7.012 | 0 | 0 | 0 | 0 | 0 | 0
CSLN13;DC SYS01 | NORTH WEST | 2024-05-02 |  | 39.6565 | 5.0626 | 18.6717 | 1.7686 | 23.7941 | 2.4053 | 74.3217 | 22.2965 | 0 | 0 | 0 | 0 | 0 | 1
CTNN01-DCSYS01a | SOUTH WEST | 2024-05-02 |  | 59.4923 | 15.1897 | 50.2697 | 10.4547 | 40.5931 | 7.0671 | 62.6343 | 31.004 | 0 | 0 | 0 | AM | 0 | 6.8
CTNN01-DCSYS01b | SOUTH WEST | 2024-05-02 |  | 68.0658 | 17.3787 | 60.7952 | 12.6437 | 53.1666 | 9.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9
CTRTK1;DC SYS01 | NORTH WEST | 2022-02-02 17:00 |  | 87.5682 | 20.9989 | 87.3086 | 20.5084 | 70.5094 | 7.1276 | 82.3339 | 13.8939 | 0 | 0 | 0 | 0 | 0 | 0
CTRTS1; DC SYS01 | NORTH WEST | 2024-05-02 |  | 3.3493 | 0.42758 | -30.2615 | -2.8664 | -22.057 | -2.2297 | 34.1947 | 6.4115 | 0 | RA | 0 | 0 | 0 | 4
CYNTN2;DC SYS01 | LONDON | 2023-07-20 |  | 41.0466 | 36.24 | 22.0371 | 14.7125 | 25.9686 | 18.258 | 27.7083 | 19.95 | 0 | 0 | 0 | 0 | 0 | 3
DBY;DC SYS01 | MIDLANDS | 2021-11-30 17:00 |  | 53.8273 | 15.4612 | 44.1348 | 10.4777 | 46.9771 | 11.7503 | 58.876 | 18.9875 | 0 | 0 | 0 | 0 | 0 | 1
DCT;DC SYS01 | THAMES VALLEY | 2023-04-28 |  | 48.1383 | 8.0805 | 40.4777 | 5.9201 | 33.8206 | 4.4489 | 80.6544 | 36.2945 | 0 | 0 | 0 | 0 | 0 | 4.4
DFSN01; DC SYS01 | SCOTLAND | 2024-04-02 |  | 34.4513 | 3.8483 | 36.388 | 4.1884 | 37.3648 | 4.3679 | 30.2667 | 3.178 | 0 | 0 | 0 | 0 | 0 | 1
DFSNC1; DC SYS01 | SCOTLAND | 2021-09-06 09:10 |  | 62.5 | 2.9975 | 69.1589 | 4.033 | 36.3426 | 1.0268 | 76.02 | 5.7015 | 0 | 0 | 0 | 0 | 0 | 0
DGS;DC SYS01 | NORTH WEST | 2024-05-02 |  | 74.6667 | 12.208 | 75.2443 | 12.5895 | 37.2516 | 2.459 | 44.7733 | 3.358 | 0 | 0 | 0 | 0 | 0 | 0
DHMNU1;DC SYS01 | NORTH EAST | 2022-01-13 13:00 |  | 75 | 6.54 | 73.6842 | 6.104 | 62.7854 | 3.6779 | 80.6222 | 9.07 | 0 | 0 | 0 | 0 | 0 | 0
DKTN08; DC SYS01 | LONDON | 2024-04-16 |  | 23.5983 | 18.0755 | -12.2262 | -6.3754 | 17.7003 | 12.5862 | 60.986 | 91.479 | 0 | RA | 0 | 0 | 0 | 7.4
DLD;DC SYS01 | SCOTLAND | 2024-05-02 |  | 64.4809 | 5.1448 | 57.7236 | 3.8695 | 47.3077 | 2.5444 | 62.2133 | 4.666 | 0 | 0 | 0 | 0 | 0 | 0
DLNTC1;DC SYS01 | NORTH EAST | 2022-02-23 11:45 |  | 72.62 | 7.9156 | 71.1789 | 7.3706 | 42.906 | 2.2428 | 90.0519 | 27.0156 | 0 | 0 | 0 | 0 | 0 | 0
DNDN71; SYS 01 | SCOTLAND | 2024-05-02 |  | 48.0792 | 12.2757 | 30.0234 | 5.6877 | 34.4309 | 6.9611 | 41.0822 | 9.2435 | 0 | RA | 0 | 0 | 0 | 4.7
DNDTC1;DCSYS01 | SCOTLAND | 2024-05-02 |  | 48.0874 | 3.8368 | 28.0303 | 1.6132 | 50.831 | 4.282 | 44.7733 | 3.358 | 0 | 0 | 0 | 0 | 0 | 0
DNFNP1; DC SYS01 | SCOTLAND | 2024-05-02 |  | 62.3126 | 4.9718 | 55.1428 | 3.6965 | 44.0912 | 2.3714 | 40.1592 | 2.018 | 0 | 0 | 0 | 0 | 0 | 0.5
DONTN1;DC SYS01 | NORTH EAST | 2022-02-10 09:30 |  | 50 | 9.81 | 14.2857 | 1.635 | 53.5617 | 11.3148 | 49.6923 | 9.69 | 0 | 0 | 0 | 0 | 0 | 0
DVSTB1; DC SYS01 | SOUTH WEST | 2021-12-23 12:00 |  | 93.1694 | 7.4338 | 85.5072 | 3.2155 | 95.1272 | 10.6395 | 92.7333 | 6.955 | 0 | 0 | 0 | 0 | 0 | 0
DWLTM1;DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | 2021-10-11 12:07 |  | -21.5494 | -1.057 | -2.7178 | -0.15775 | -15.0077 | -0.778 | #DIV/0! | -5.962 | 0 | 0 | 0 | 0 | 0 | 4
ECBTC1; DC SYS01 | NORTH EAST | 2022-11-14 |  | 27.37 | 0.7876 | 8.6938 | 0.199 | 28.6436 | 0.83896 | 38.0741 | 1.285 | 0 | 0 | 0 | 0 | 0 | 1
EDBCD1;DC SYS01 | SCOTLAND | 2021-08-23 12:00 |  | 18.6667 | 3.052 | -19.0244 | -2.1255 | 7.8371 | 1.1308 | -77.3067 | -5.798 | 0 | 0 | 0 | 0 | 0 | 0
EDBTG1;DC SYSA | SCOTLAND | 2024-05-03 |  | 40.7019 | 31.8257 | 14.3586 | 7.7738 | 34.7935 | 24.7407 | 55.8414 | 58.6335 | 0 | RA | PX | 0 | OPEX | 22.55
EDBTG1;DC SYSB | SCOTLAND | 2024-05-03 |  | 36.7412 | 28.7287 | 8.6383 | 4.6768 | 30.4381 | 21.6437 | 52.8919 | 55.5365 | 0 | 0 | 0 | 0 | 0 | 22.05
EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | SCOTLAND | 2024-05-03 |  | 50.9172 | 33.3132 | 41.839 | 23.101 | 25.8127 | 11.1734 | -16.3037 | -11.005 | P-Core | 0 | 0 | 0 | 0 | 7.7515
EDBTN1;DC SYSB | SCOTLAND | 2024-05-03 |  | 29.0926 | 19.0342 | 15.9778 | 8.822 | -7.1745 | -3.1056 |  |  | 0 | 0 | 0 | 0 | 0 | 7.7515
EGNTM1;DC SYS01 | SCOTLAND | 2022-01-03 08:10 |  | 26.2793 | 1.289 | 37.7008 | 2.1883 | 30.2469 | 1.568 | 28.0398 | 1.409 | 0 | 0 | 0 | 0 | 0 | 1
EVMN01;DC SYS01 | MIDLANDS | 2024-05-03 |  | 71.248 | 9.0956 | 61.2494 | 5.8016 | 63.6901 | 6.4383 | 67.3733 | 7.5795 | 0 | 0 | 0 | 0 | 0 | 1
EXR;DC SYS01 | SOUTH WEST | 2021-08-11 12:00 |  | 48.7613 | 13.2279 | 27.1714 | 5.1859 | 39.5189 | 9.0824 | 72.3383 | 36.35 | 0 | 0 | 0 | 0 | 0 | 3
EXRN03-DCSYSa | SOUTH WEST | 2023-05-02 |  | 72.3914 | 17.3279 | 64.8531 | 12.194 | 62.0411 | 10.8011 | 74.1134 | 37.242 | 0 | 0 | 0 | AM | 0 | 5.9
EXRN03-DCSYSb | SOUTH WEST | 2023-05-02 |  | 73.2646 | 17.5369 | 65.9646 | 12.403 | 63.2415 | 11.0101 |  |  | 0 | 0 | 0 | 0 | 0 | 5.8
FKE;DC SYS01 | SOUTH EAST | 2021-03-31 09:00 |  | 73.9359 | 22.4169 | 63.3283 | 13.6468 | 70.352 | 18.7519 | 64.8778 | 14.5975 | 0 | 0 | 0 | 0 | 0 | 0
FLNTT1;DC SYS01 | NORTH EAST | 2022-05-19 09:30 |  | 85.2273 | 4.0875 | 81.4286 | 3.1065 | 81.1921 | 3.0585 | 85.9005 | 4.3165 | 0 | 0 | 0 | 0 | 0 | 0
FMYN31; DC SYS01 | THAMES VALLEY | 2024-05-03 |  | 70.4007 | 6.7406 | 66.581 | 5.6462 | 63.7158 | 4.9766 | 74.8089 | 8.416 | 0 | 0 | 0 | 0 | 0 | 0
FRNN03-DCSYS01a | SOUTH WEST | 2024-05-03 |  | 73.6305 | 19.9744 | 68.6138 | 15.6384 | 58.9106 | 10.2561 | 86.8387 | 97.6935 | 0 | 0 | 0 | AM | 0 | 5.9
FRNN03-DCSYS01b | SOUTH WEST | 2024-05-03 |  | 71.7892 | 19.4749 | 66.4223 | 15.1389 | 56.0415 | 9.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8
GCRTB1;DC SYS01 | SOUTH WEST | 2024-05-03 |  | 45.5788 | 16.0012 | 13.4848 | 2.9779 | 46.2628 | 16.4481 | 57.5433 | 25.8945 | 0 | RA | 0 | 0 | 0 | 3.9
GFDCD1;DC SYS01A | SOUTH | 2024-05-03 |  | 61.6033 | 40.3047 | 48.818 | 23.9612 | 52.8946 | 28.2089 | 69.5089 | 125.116 | 0 | RA | 0 | 0 | 0 | 7.3
GFDCD1;DC SYS01B | SOUTH | 2024-05-03 |  | 54.5098 | 35.6637 | 39.3625 | 19.3202 | 44.1922 | 23.5679 |  |  | 0 | 0 | 0 | 0 | 0 | 6.6
GLWN07;DC SYS A | SCOTLAND | 2024-05-03 |  | 30.3668 | 25.6828 | 5.1942 | 3.2266 | 17.1779 | 12.2147 | -16.9667 | -15.27 | P-Core | RA | PX | 0 | OPEX | 11.75
GLWN07;DC SYS B | SCOTLAND | 2024-05-03 |  | 45.1642 | 38.1978 | 25.341 | 15.7416 | 34.7781 | 24.7297 |  |  | 0 | 0 | 0 | 0 | 0 | 13.95
GLWTO1;DC SYS01 | SCOTLAND | 2024-05-03 |  | 50.3389 | 14.4592 | 27.053 | 5.2901 | 46.4835 | 12.3899 | 36.6022 | 8.2355 | 0 | RA | 0 | 0 | 0 | 4.4
GLWTW1;DC SYS01 | SCOTLAND | 2024-05-03 |  | 34.9038 | 18.9373 | -0.56578 | -0.1987 | 33.7742 | 18.0119 | 43.9389 | 27.6815 | 0 | 0 | 0 | 0 | 0 | 3
GRSTB1;DC SYS01 | SCOTLAND | 2024-05-03 |  | 0.03196 | 0.00102 | -10.04 | -0.2911 | -77.9618 | -1.3977 | 36.5075 | 1.8345 | 0 | 0 | 0 | 0 | 0 | 2.7
GWK;DC SYS01 | SOUTH EAST | 2024-05-03 |  | 24.2027 | 2.77 | 14.0063 | 1.4129 | -2.9796 | -0.251 | 27.7083 | 3.325 | 0 | 0 | 0 | 0 | 0 | 0.5
HHD;DC SYS01 | NORTHERN HOME COUNTIES | 2023-07-04 |  | 45.2229 | 12.9897 | 11.7943 | 2.1039 | 44.1819 | 12.454 | 30.0711 | 6.766 | 0 | 0 | 0 | 0 | 0 | 2
HLDA11;DC SYS01 | LONDON | 2024-05-03 |  | 47.3068 | 5.2843 | 15.7566 | 1.1009 | 62.3202 | 9.7351 | 87.9262 | 42.864 | 0 | 0 | 0 | 0 | 0 | 0
HLDA12;DC SYS01 | LONDON | 2024-05-03 |  | 45.3552 | 5.0663 | 12.6365 | 0.8829 | 60.9247 | 9.5171 | 87.479 | 42.646 | 0 | 0 | 0 | 0 | 0 | 0
HLWN02;DC SYS01 | ANGLIA | 2022-11-15 |  | 53.6056 | 13.6867 | 47.7024 | 10.8047 | 17.9038 | 2.5833 | 82.4511 | 55.6545 | 0 | 0 | 0 | 0 | 0 | 1
HRWN02;DC SYS01 | LONDON | 2020-08-19 |  | 35.2581 | 22.5054 | 12.2388 | 5.763 | 22.5114 | 12.0054 | 38.7778 | 26.175 | 0 | RA | 0 | 0 | 0 | 5.9
HTE;DC SYS01 | NORTH EAST | 2022-04-01 13:00 |  | 54.8547 | 7.175 | 40.1389 | 3.9595 | 41.5855 | 4.2038 | 34.3889 | 3.095 | 0 | 0 | 0 | 0 | 0 | 1
IGNN01;DC SYS01 | LONDON | 2024-05-03 |  | 0.30957 | 0.1235 | -41.6959 | -11.703 | -11.8607 | -4.2169 | 45.8905 | 33.7295 | 0 | RA | 0 | 0 | 0 | 4.4
INVN41;DC SYS01 | SCOTLAND | 2024-05-03 |  | -9.0468 | -1.1549 | -46.9685 | -4.4489 | -37.7117 | -3.8122 | -23.7422 | -2.671 | 0 | RA | 0 | 0 | 0 | 6.4
INVTL1;DC SYS01 | SCOTLAND | 2024-05-03 |  | 18.2913 | 2.3351 | -0.94647 | -0.0978 | 7.1314 | 0.801 | 0.65714 | 0.069 | 0 | 0 | 0 | 0 | 0 | 4
IODN01;DC SYS01 | LONDON | 2021-06-22 |  | 25.3797 | 11.5635 | 3.2828 | 1.154 | 4.374 | 1.5551 | 77.3343 | 116.0015 | 0 | RA | 0 | 0 | OPEX | 10.4
IODTA1;DC SYS01 | LONDON | 2024-05-03 |  | 40.0286 | 19.8016 | 5.0996 | 1.5942 | 39.76 | 19.581 | 51.1654 | 31.083 |  |  |  |  | OPEX | 1
IPWTN1;DC SYS01 | ANGLIA | 2022-10-20 |  | 44.2711 | 17.6615 | 20.7892 | 5.835 | 37.4677 | 13.3211 | 1.1889 | 0.2675 | 0 | RA | 0 | 0 | 0 | 6.7
IVER02; DC SYS01 | THAMES VALLEY | 2021-07-06 14:00 |  | 15.4713 | 0.98754 | -14.5833 | -0.6867 | 41.4459 | 3.8191 | 40.05 | 3.6045 | 0 | 0 | 0 | 0 | 0 | 0
KLNN01;DC SYS01 | ANGLIA | 2021-08-05 17:00 |  | 86.6667 | 5.668 | 87.9336 | 6.3547 | 51.361 | 0.9208 | 76.7467 | 2.878 | 0 | 0 | 0 | 0 | 0 | 0
KNLTS1;DC SYS01 | NORTH WEST | 2024-05-03 |  | 42.7193 | 5.4536 | 22.7996 | 2.1596 | 27.662 | 2.7963 | 67.5 | 15.1875 | 0 | 0 | 0 | 0 | 0 | 0.5
LCT;DC SYS01 | MIDLANDS | 2024-05-03 |  | 41.6079 | 45.8134 | 16.059 | 12.3003 | 32.7541 | 31.3162 | 22.0679 | 18.206 | 0 | RA | 0 | 0 | 0 | 13.5
LDMS13;DC SYS01 A | NORTH EAST | 2022-06-01 13:00 |  | 85.3896 | 14.3335 | 86.1538 | 15.26 | 54.4009 | 2.9259 | 70.7062 | 16.9695 | 0 | 0 | 0 | 0 | 0 | 0
LDMS13;DC SYS01 B | NORTH EAST | 2022-05-19 15:30 |  | 72.7273 | 12.208 | 74.1538 | 13.1345 | 14.8817 | 0.8004 |  |  | 0 | 0 | 0 | 0 | 0 | 0
LDSCD2;DC SYS A | NORTH EAST | 2024-05-03 |  | 34.7226 | 56.62 | 23.1063 | 31.986 | 0.20326 | 0.2168 | 9.9236 | 19.351 | P-Core | RA | PX | 0 | OPEX | 17.5
LDSCD2;DC SYS B | NORTH EAST | 2024-05-03 |  | 58.1747 | 96.257 | 51.0668 | 72.2225 | 35.1167 | 37.4558 |  |  | 0 | 0 | 0 | 0 | 0 | 20.7
LDSN14; DC SYS01 | NORTH EAST | 2022-03-17 16:00 |  | 63.0803 | 11.345 | 36.3787 | 3.7967 | 64.6658 | 12.152 | 72.3333 | 17.36 | 0 | 0 | 0 | 0 | 0 | 0.1
LDSTS1;DC SYS01 | NORTH EAST | 2024-05-03 |  | 38.6628 | 20.9768 | 5.2415 | 1.8408 | 37.5984 | 20.0514 | 75.3489 | 101.721 | 0 | RA | 0 | 0 | 0 | 8.1
LIVN01;DC SYS01 | SCOTLAND | 2024-05-03 |  | 43.7784 | 23.7523 | 13.1444 | 4.6163 | 42.8028 | 22.8269 | 54.8096 | 36.9965 | 0 | 0 | 0 | 0 | 0 | 2
LLDTE1;DC SYS01 | NORTH WEST | 2024-05-03 |  | 41.0847 | 11.1454 | -31.9788 | -3.8726 | 55.0467 | 19.5711 | 28.9667 | 6.5175 | 0 | RA | 0 | 0 | 0 | 5.9
LMSCN2;DC SYS01 | MIDLANDS | 2022-05-26 14:30 |  | 51.5027 | 8.2186 | -27.9279 | -1.6895 | 64.2428 | 13.9042 | 63.1476 | 13.261 | 0 | 0 | 0 | 0 | 0 | 0
LPLTB1;DC SYS01 | NORTH WEST | 2024-05-03 |  | 62.4317 | 8.9663 | 69.5759 | 12.3388 | -56.1198 | -1.9395 | 52.04 | 5.8545 | 0 | 0 | 0 | 0 | 0 | 0
LPLTK1;DC SYS01 | NORTH WEST | 2024-05-03 |  | 52.1595 | 20.8085 | 32.0014 | 8.982 | 46.3191 | 16.4681 | 49.1053 | 18.4145 | 0 | RA | 0 | 0 | 0 | 1.7
LSWN01;DC SYS01 | LONDON | 2023-01-18 |  | 19.5584 | 21.745 | 6.228 | 5.94 | 21.2831 | 24.181 | -25.5228 | -18.185 | 0 | 0 | 0 | 0 | 0 | 11.5
LTNDN1;DC SYS01 | NORTHERN HOME COUNTIES | 2022-04-25 17:00 |  | 60.8563 | 21.89 | 48.8419 | 13.4425 | 49.9346 | 14.0432 | 37.4222 | 8.42 | 0 | 0 | 0 | 0 | 0 | 1
MCRCD2;DC SYS01 [Rect1&2] | NORTH WEST | 2024-05-03 |  | 70.7376 | 53.0537 | 56.2381 | 28.2039 | 69.1353 | 49.1602 | 31.6839 | 28.5155 | 0 | 0 | 0 | 0 | 0 | 2
MCRCD2;DC SYS02 [Rect 3&4] | NORTH WEST | 2024-05-03 |  | 39.5693 | 25.8887 | -3.5482 | -1.3548 | 44.3973 | 31.5697 |  |  | 0 | RA | PX | 0 | OPEX | 19.1
MCRCD2;DC SYS03 [Rect5] | NORTH WEST | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MCRN11;DC SYS01a | NORTH WEST | 2024-05-03 |  | 46.3638 | 46.6109 | 41.9982 | 39.0441 | -1.1093 | -0.5916 | 18.3036 | 20.5915 | P-Core | 0 | 0 | 0 | 0 | 4
MCRN11;DC SYS01b | NORTH WEST | 2024-05-03 |  | 62.2148 | 62.5464 | 59.1394 | 54.9796 | 28.7714 | 15.3439 |  |  | 0 | 0 | 0 | 0 | 0 | 0
MCRN12;DC SYS01 A | NORTH WEST | 2024-05-03 |  | 41.6281 | 82.854 | 28.1031 | 45.4125 | 18.3064 | 26.0344 | 37.1412 | 139.2795 | P-Core | RA | PX | 0 | OPEX | 18.625
MCRN12;DC SYS01 B | NORTH WEST | 2024-05-03 |  | 39.9397 | 79.4935 | 26.0235 | 42.052 | 15.9435 | 22.6739 |  |  | 0 | 0 | 0 | 0 | 0 | 18.225
MDBTD1;DC SYS01 | NORTH EAST | 2021-07-14 11:00 |  | 72.8175 | 20.0015 | 73.1898 | 20.383 | 26.1386 | 2.6423 | 66.8156 | 15.0335 | 0 | 0 | 0 | 0 | 0 | 0
MDE;DC SYS01 | SOUTH EAST | 2022-04-12 |  | 64.8372 | 22.7622 | 44.1005 | 9.7389 | 65.2792 | 23.2091 | 63.4237 | 21.4055 | 0 | 0 | 0 | 0 | 0 | 0.3
MDFTB1;DC SYS01 | SCOTLAND | 2022-01-03 11:40 |  | -20.4383 | -1.0025 | 0.097239 | 0.00575 | -70.9346 | -2.4515 | 1.5417 | 0.0925 | 0 | 0 | 0 | 0 | 0 | 4
MKSTN1;DC SYS01 | NORTHERN HOME COUNTIES | 2021-12-23 10:00 |  | 41.4095 | 18.5023 | 23.1196 | 7.8726 | 26.3675 | 9.3746 | 51.5204 | 27.821 | 0 | 0 | 0 | 0 | 0 | 1
NBYCD1;DC SYS01 | THAMES VALLEY | 2023-06-21 |  | 45.0427 | 12.9615 | 18.7187 | 3.642 | 41.6146 | 11.2719 | 52.0773 | 17.1855 | 0 | 0 | 0 | 0 | 0 | 0.5
NECCD1;DC SYS01 | MIDLANDS | 2022-03-04 09:00 |  | 74.1413 | 8.2818 | 71.597 | 7.2812 | 59.7208 | 4.2827 | 74.3244 | 8.3615 | 0 | 0 | 0 | 0 | 0 | 0
NGM;DC SYS03 | MIDLANDS | 2021-10-29 17:00 |  | 31.9958 | 15.3173 | 11.5039 | 4.232 | 14.1197 | 5.3525 | 67.3629 | 67.1945 | 0 | 0 | 0 | 0 | 0 | 1
NGMTL1;DC SYS01 | MIDLANDS | 2022-06-17 15:16 |  | 59.225 | 12.911 | 49.2691 | 8.6328 | 41.3781 | 6.2742 | 80.2468 | 36.111 | 0 | 0 | 0 | 0 | 0 | 0
NRWN51;DC SYS01 | ANGLIA | 2024-05-03 |  | 18.5811 | 1.7791 | -43.6111 | -2.3673 | 57.7001 | 10.6336 | 30.7067 | 3.4545 | 0 | RA | 0 | 0 | 0 | 2.4
NRWTN1;DC SYS01 | ANGLIA | 2022-01-04 18:00 |  | 50.9104 | 13.8109 | 15.9447 | 2.5261 | 52.7565 | 14.871 | 40.8133 | 9.183 | 0 | 0 | 0 | 0 | 0 | 1
NULTB1;DC SYS01 | NORTH WEST | 2024-05-03 |  | 54.8522 | 8.7531 | 38.2277 | 4.4585 | 51.6886 | 7.7081 | 31.3857 | 3.2955 | 0 | RA | 0 | 0 | 0 | 1.7
NWCN05;DC SYS01a | NORTH EAST | 2024-05-03 |  | 38.1587 | 18.8766 | 14.2498 | 5.0837 | 27.5922 | 11.6576 | -25.8133 | -11.616 | 0 | RA | 0 | 0 | OPEX | 10.1
NWCN05;DC SYS01b | NORTH EAST | 2024-05-03 |  | 29.0947 | 10.6785 | -48.3855 | -8.4859 | 43.0617 | 19.6816 | [7 empty] | 11.2
NWCNY1;DC SYS01 | NORTH EAST | 2022-03-18 12:00 |  | 60.9745 | 11.2401 | 56.5504 | 9.3631 | 28.8343 | 2.9148 | 68.0267 | 15.306 | 0 | 0 | 0 | 0 | 0 | 0
NWPDN1;DC SYS01 | WALES | 2021-12-02 14:00 |  | 30 | 3.597 | 10.1097 | 0.94394 | 28.0436 | 3.271 | 62.6978 | 14.107 | 0 | 0 | 0 | 0 | 0 | 0
OHB;DC SYS01;PSU1 | WALES | 2021-06-08 10:00 |  | 55.8964 | 14.6225 | 44.1432 | 9.118 | 38.6042 | 7.2545 | 52.5611 | 23.6525 | 0 | 0 | 0 | 0 | 0 | 2
OHB;DC SYS02;PSU2 | WALES | 2021-06-08 12:00 |  | 50 | 9.81 | 21.3974 | 2.6705 | 47.7969 | 8.982 |  |  | 0 | 0 | 0 | 0 | 0 | 0
OKNN01-DCSYS01a | SOUTH WEST | 2024-05-03 |  | 64.4743 | 21.606 | 56.0128 | 15.1597 | 48.1995 | 11.0774 | 46.3077 | 18.06 | 0 | RA | 0 | AM | 0 | 7
OKNN01-DCSYS01b | SOUTH WEST | 2024-05-03 |  | 73.0387 | 24.476 | 66.617 | 18.0297 | 60.6873 | 13.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4
PCOTN1;DC SYS A;FLAG | SOUTH WEST | 2020-01-10 |  | 55.5483 | 12.715 | 8.9282 | 0.9975 | 63.8199 | 17.9482 | 72.1806 | 83.91 | 0 | 0 | 0 | 0 | 0 | 2
PCOTN1;DC SYS A;GEMINI | SOUTH WEST | 2021-09-22 15:00 |  | 90.5505 | 29.61 | 83.8008 | 15.985 | 91.3089 | 32.4636 |  |  | 0 | 0 | 0 | 0 | 0 | 2
PCOTN1;DC SYS B;FLAG | SOUTH WEST | 2020-01-10 |  | 64.2857 | 14.715 | 26.8293 | 2.9975 | 70.9315 | 19.9482 |  |  | 0 | 0 | 0 | 0 | 0 | 0
PCOTN1;DC SYS B;GEMINI | SOUTH WEST | 2021-09-22 16:00 |  | 62.963 | 18.53 | 27.2727 | 4.0875 | 69.3421 | 24.6536 |  |  | 0 | 0 | 0 | 0 | 0 | 0
PLY-DCSYS01a | SOUTH WEST | 2024-05-03 |  | 66.3753 | 30.7165 | 62.5015 | 25.9358 | 41.6213 | 11.0939 | 84.4122 | 84.2645 | 0 | RA | 0 | AM | 0 | 11.8
PLY-DCSYS01b | SOUTH WEST | 2024-05-03 |  | 51.7903 | 23.967 | 46.2362 | 19.1863 | 16.299 | 4.3444 | 77.6509 | 77.515 | 0 | 0 | 0 | 0 | 0 | 12.5
PNRTN1;DC SYS01 | NORTH WEST | 2022-02-24 14:00 |  | 92 | 4.0112 | 15.7895 | 0.0654 | 95.6356 | 7.6432 | 96.1244 | 8.6512 | 0 | 0 | 0 | 0 | 0 | 0
POLN02-DCSYS01a | SOUTH WEST | 2024-05-03 |  | 49.4052 | 24.4401 | 37.4845 | 15.0072 | 29.6035 | 10.5251 | 44.1289 | 29.787 | 0 | RA | 0 | AM | 0 | 10.15
POLN02-DCSYS01b | SOUTH WEST | 2024-05-03 |  | 74.3585 | 36.7841 | 68.317 | 27.3512 | 64.3229 | 22.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.45
PRDTB1;DC SYS01 | SCOTLAND | 2022-01-03 14:20 |  | 54.0571 | 2.6515 | 27.8384 | 0.86935 | 55.8677 | 2.8527 | 55.1542 | 2.7715 | 0 | 0 | 0 | 0 | 0 | 1
PRLN02;DC SYS01 | LONDON | 2021-12-01 |  | 13.1336 | 2.9341 | -2.4993 | -0.4732 | 54.7244 | 23.4565 | 48.2493 | 18.0935 | 0 | 0 | 0 | 0 | 0 | 5.4
PTBTN1;DC SYS01 | ANGLIA | 2022-08-09 |  | 40.7041 | 16.2385 | 28.7281 | 9.535 | 9.4159 | 2.4589 | 61.0609 | 37.0945 | 0 | 0 | 0 | 0 | 0 | 3
PTHTL1;DC SYS01 | SCOTLAND | 2024-05-03 |  | 39.3571 | 5.3195 | 20.845 | 2.1585 | 23.8017 | 2.5603 | 27.1422 | 3.0535 | 0 | 0 | 0 | 0 | 0 | 4
PTMDN1;DC SYS01 | SOUTH | 2023-03-07 |  | 61.5002 | 10.7954 | 40.0966 | 4.5235 | 61.9379 | 10.9972 | 43.6833 | 5.242 | 0 | 0 | 0 | 0 | 0 | 0
PTMN03;DC SYS01 | SOUTH | 2024-05-03 |  | 61.5737 | 33.4073 | 40.6361 | 14.2713 | 60.9069 | 32.4819 | 53.67 | 24.1515 | 0 | RA | 0 | 0 | 0 | 2.7
RATE02;DC SYS01 | MIDLANDS | 2021-10-21 16:00 |  | 79.1667 | 5.1775 | 77.2727 | 4.6325 | 62.0008 | 2.2231 | 53.4933 | 4.012 | 0 | 0 | 0 | 0 | 0 | 0
RATE02;DC SYS02 | MIDLANDS | 2021-10-21 17:00 |  | 67.5 | 4.4145 | 66.9492 | 4.3055 | 45.5737 | 1.7798 |  |  | 0 | 0 | 0 | 0 | 0 | 0
RCR;DC SYS01 | SOUTH EAST | 2022-11-30 |  | 56.138 | 19.7082 | 30.2712 | 6.6849 | 56.6893 | 20.1551 | 54.3748 | 18.3515 | 0 | RA | 0 | 0 | 0 | 2.7
RDGCD2;DC SYS01 | THAMES VALLEY | 2021-08-20 09:00 |  | 38.9978 | 22.444 | 10.5301 | 4.132 | 34.1689 | 18.2224 | -11.454 | -3.608 | 0 | 0 | 0 | AM | 0 | 12
RDG;DC SYS01 | THAMES VALLEY | 2023-03-29 |  | 65.9091 | 23.7075 | 62.7483 | 20.6555 | 34.7462 | 6.5295 | 65.9375 | 23.7375 | 0 | 0 | 0 | 0 | 0 | 0
RFDN11;DC SYS01 | LONDON | 2024-05-03 |  | 83.3504 | 10.6406 | 77.5604 | 7.3466 | 78.9738 | 7.9833 | 81.1067 | 9.1245 | 0 | 0 | 0 | 0 | 0 | 0
SBHN01;DC SYS01 | NORTH EAST | 2022-05-17 13:30 |  | 64.2857 | 14.715 | 63.0542 | 13.952 | 19.1299 | 1.9338 | 87.8889 | 59.325 | 0 | 0 | 0 | 0 | 0 | 0
SDN;DC SYS01 | SOUTH WEST | 2023-09-13 |  | 59.5238 | 27.25 | 17.0732 | 3.815 | 67.0557 | 37.7164 | 70.2329 | 43.72 | 0 | 0 | 0 | 0 | 0 | 0
SDNN06;DC SYS02 | SOUTH WEST | 2022-10-12 |  | 19.7936 | 25.9003 | -2.3668 | -2.4266 | 32.5435 | 50.6328 | 60.4658 | 248.5145 | 0 | 0 | 0 | 0 | 0 | 36.5
SDNN06;DC SYS03 | SOUTH WEST | 2022-10-12 |  | 41.4822 | 40.7845 | 36.2139 | 32.664 | 32.4819 | 27.6785 |  |  | P-Core | RA | PX | 0 | OPEX | 10.5
SDNN11;DC SYS01 | SOUTH WEST | 2022-06-07 13:30 |  | 16.3306 | 0.8829 | 1.1905 | 0.0545 | 26.3638 | 1.6195 | 98.8994 | 406.4765 | 0 | 0 | 0 | 0 | 0 | 0
SDNN13;DC SYS01 | SOUTH WEST | 2023-08-23 |  | 32.6672 | 8.8619 | 25.8832 | 6.3789 | 20.6709 | 4.7596 | 51.2907 | 19.234 | 0 | 0 | 0 | 0 | 0 | 10.2
SHD;DC SYS01 | NORTH EAST | 2024-05-03 |  | 56.4741 | 26.1345 | 44.1205 | 15.9038 | 43.3461 | 15.4111 | 68.0278 | 42.8575 | 0 | 0 | 0 | 0 | 0 | 0.25
SHDTR1;DC SYS01 | NORTH EAST | 2024-05-03 |  | 46.1598 | 18.415 | 23.4738 | 6.5885 | 39.587 | 14.0746 | 80.9076 | 91.021 | 0 | RA | 0 | 0 | 0 | 7.2
SHTN03;DC SYS02 | SOUTH | 2024-05-03 |  | 49.3502 | 28.3504 | 25.6006 | 10.0122 | 45.4401 | 24.2334 | 65.5147 | 55.278 | 0 | RA | 0 | 0 | 0 | 3.7
SLO;DC SYS01 | THAMES VALLEY | 2024-05-03 |  | 41.516 | 22.5248 | 9.6493 | 3.3888 | 40.5011 | 21.5994 | 49.6333 | 31.269 | 0 | 0 | 0 | 0 | 0 | 3.5
SMHN02;DC SYS01 | LONDON | 2022-03-23 08:30 |  | 44.1176 | 24.525 | 35.5932 | 17.1675 | 9.3765 | 3.2142 | 70.4143 | 73.935 | 0 | 0 | 0 | 0 | 0 | 0
SNDTM1;DC SYS01 | NORTH EAST | 2024-03-05 |  | 61.9205 | 8.1532 | 61.9835 | 8.175 | 4.0787 | 0.2132 | 88.8578 | 39.986 | 0 | 0 | 0 | 0 | 0 | 0
SOL;DC SYS01 | MIDLANDS | 2024-05-03 |  | 55.0816 | 18.492 | 25.217 | 5.085 | 57.5852 | 20.4736 | 66.4889 | 29.92 | 0 | 0 | 0 | 0 | 0 | 2
SOSTN1;DC SYS01 | ANGLIA | 2021-02-04 |  | 36.7421 | 5.2768 | -4.5779 | -0.3977 | 37.0357 | 5.3438 | 53.4103 | 10.415 | 0 | 0 | 0 | 0 | 0 | 2
SOT;DC SYS01 | MIDLANDS | 2024-05-03 |  | 27.5495 | 4.8359 | -43.5108 | -3.8558 | 39.7982 | 8.4073 | 29.3472 | 5.2825 | 0 | 0 | 0 | 0 | 0 | 1
SQYN01;DC SYS01 | LONDON | 2024-05-03 |  | 63.6033 | 28.4188 | 48.0872 | 15.0641 | 59.325 | 23.7191 | 45.4595 | 85.2365 | 0 | 0 | 0 | 0 | 0 | 4
SQYN01;DC SYS02 | LONDON | 2024-05-03 |  | 38.0589 | 26.7224 | 17.7659 | 9.3958 | 22.6777 | 12.7554 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SQYN01;DC SYS03 | LONDON | 2024-05-03 |  | 57.0333 | 56.4271 | 53.271 | 48.4614 | 20.2894 | 10.8204 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SQYN02;DC SYS08a | LONDON | 2024-05-03 |  | 37.5416 | 37.1426 | 22.1635 | 17.5957 | 14.3456 | 10.3495 | 37.7296 | 140.92 | P-Core | 0 | 0 | 0 | 0 | 17.05
SQYN02;DC SYS08b | LONDON | 2024-05-03 |  | 39.6809 | 39.8924 | 14.7902 | 10.5256 | 31.7757 | 28.2435 |  |  | P-Core | RA | PX | 0 | OPEX | 16.55
SQYN02;DC SYS09a | LONDON | 2024-05-03 |  | 51.3919 | 58.2265 | 27.7488 | 21.1512 | 48.3667 | 51.5883 |  |  | P-Core | 0 | 0 | 0 | 0 | 5.75
SQYN02;DC SYS09b | LONDON | 2024-05-03 |  | 51.3919 | 58.2265 | 27.7488 | 21.1512 | 48.3667 | 51.5883 |  |  | P-Core | 0 | 0 | 0 | 0 | 5.75
STEDN1;DC SYS01 | NORTHERN HOME COUNTIES | 2024-05-03 |  | 66.1575 | 11.6129 | 71.9217 | 15.2164 | 54.0479 | 6.9871 | 47.1956 | 5.3095 | 0 | 0 | 0 | 0 | 0 | 0
STGCD1;DC SYS01 | SCOTLAND | 2022-11-08 |  | 39.9847 | 6.5375 | 29.6696 | 4.1395 | 2.9311 | 0.2963 | 34.5833 | 5.1875 | 0 | 0 | 0 | 0 | 0 | 3
SWNN03;DC SYS01 | WALES | 2024-05-03 |  | 7.2612 | 1.0428 | -94.8846 | -6.4847 | 23.4962 | 4.0906 | 55.6033 | 16.681 | 0 | RA | 0 | 0 | 0 | 3.4
SWY;DC SYS01 | MIDLANDS | 2021-11-02 10:00 |  | 45.8954 | 18.3095 | 35.8526 | 12.0638 | 35.3634 | 11.8091 | 52.6266 | 23.978 | 0 | 0 | 0 | 0 | 0 | 3
TELHS1;DC SYS A;EXT ROOM | LONDON | 2022-01-26 10:40 |  | 10.4083 | 1.1345 | -48.0855 | -3.171 | 30.4452 | 4.2745 | 17.5696 | 4.4802 | 0 | 0 | 0 | 0 | 0 | 1.1
TELHS1;DC SYS B;EXT ROOM | LONDON | 2021-11-04 13:00 |  | 34.25 | 3.7332 | -8.6777 | -0.57225 | 48.9548 | 6.8733 |  |  | 0 | 0 | 0 | 0 | 0 | 0
TELHS1;SYS;A;DC PER02;9D | LONDON | 2023-05-12 |  | 73.5 | 8.0115 | 44.3277 | 2.2999 | 82.8555 | 13.9595 |  |  | 0 | 0 | 0 | 0 | 0 | 0
TELHS1;SYS;B;DC PER03;1L | LONDON | 2023-05-12 |  | 81.6667 | 5.341 | 52.9914 | 1.3516 | 89.3251 | 10.033 |  |  | 0 | 0 | 0 | 0 | 0 | 0
TELHS2;DC SYS01 | LONDON | 2022-02-10 17:00 |  | 93.3333 | 13.734 | 91.4081 | 10.4367 | 89.6592 | 8.5057 | 92.7333 | 12.519 | 0 | 0 | 0 | 0 | 0 | 0
TGY;DC SYSA | NORTH EAST | 2024-05-03 |  | 53.2411 | 42.48 | 44.3455 | 29.727 | 30.0437 | 16.0224 | 11.9945 | 10.957 | P-Core | 0 | PX | 0 | OPEX | 8.205
TGY;DC SYSB **DO NOT CONNECT LOADS** | NORTH EAST | 2024-05-03 |  | 46.0007 | 36.703 | 35.7276 | 23.95 | 19.2112 | 10.2454 |  |  | 0 | 0 | 0 | 0 | 0 | 8.205
THOTC1;DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | 2021-10-12 16:50 |  | 86.6667 | 2.834 | 84.3137 | 2.3435 | 85.1142 | 2.493 | 88.3733 | 3.314 | 0 | 0 | 0 | 0 | 0 | 0
TNTTN1-DCSYS01a | SOUTH WEST | 2024-05-03 |  | 59.2148 | 19.8435 | 49.5006 | 13.3972 | 40.5306 | 9.3149 | 59.5037 | 20.0825 | 0 | 0 | 0 | 0 | 0 | 7.4
TNTTN1-DCSYS01b | SOUTH WEST | 2024-05-03 |  | 64.6623 | 21.669 | 56.2456 | 15.2227 | 48.4736 | 11.1404 | 64.9126 | 21.908 | 0 | 0 | 0 | 0 | 0 | 7.7
TRON01;DC SYS01 | SOUTH WEST | 2024-05-03 |  | 67.8962 | 5.4173 | 62.6984 | 4.3055 | 54.1955 | 3.0307 | 85.7694 | 15.4385 | 0 | 0 | 0 | 0 | 0 | 0
VHXN02;DC SYS01 | LONDON | 2022-03-07 14:30 |  | 31.9498 | 21.9232 | -10.7237 | -4.5224 | 34.3322 | 24.4127 | 30.823 | 20.8055 | 0 | RA | 0 | 0 | 0 | 7.4
WADN01;DC SYS01 | LONDON | 2022-05-11 14:00 |  | 97.0068 | 137.7716 | 96.3507 | 112.2373 | 95.5538 | 91.3592 | 95.2767 | 85.749 | 0 | 0 | 0 | 0 | 0 | 0
WAHP; DC SYS A (Feeds WAHP06) | LONDON | 2024-05-03 |  | 37.4408 | 39.4327 | 14.5984 | 11.2627 | 25.8725 | 22.9965 | -11.676 | -13.1355 | P-Core | RA | PX | 0 | OPEX | 10.025
WAHP; DC SYS B (Feeds WAHP06) | LONDON | 2024-05-03 |  | 43.2701 | 45.5722 | 22.5563 | 17.4022 | 32.7798 | 29.136 |  |  | 0 | 0 | 0 | 0 | 0 | 11.025
WAHP;DC SYS A Tx | LONDON | 2024-05-03 |  | 66.8852 | 62.9723 | 67.669 | 65.2548 | 9.0483 | 3.1017 | 30.9589 | 27.863 | 0 | 0 | 0 | 0 | 0 | 11.83
WAHP;DC SYS B Tx | LONDON | 2024-05-03 |  | 67.1168 | 63.1903 | 67.8951 | 65.4728 | 9.6843 | 3.3197 |  |  | 0 | 0 | 0 | 0 | 0 | 11.83
WAIP;DC SYS01;GND | LONDON | 2022-04-22 14:30 |  | 80.1948 | 13.4615 | 83.2877 | 16.568 | -47.7083 | -1.0738 | 97.0449 | 109.1755 | 0 | 0 | 0 | 0 | 0 | 0
WCKTR1;DCSYS01 | SCOTTISH HIGHLANDS & ISLANDS | 2024-05-03 |  | 23.1296 | 1.1073 | 5.031 | 0.19495 | 12.6306 | 0.532 | 26.7662 | 1.345 | 0 | 0 | 0 | 0 | 0 | 1.5
WHD;DC SYS01 | NORTHERN IRELAND | 2022-06-08 14:00 |  | 71.875 | 1.2535 | 10 | 0.0545 | 81.7604 | 2.1987 | 91.825 | 5.5095 | 0 | 0 | 0 | 0 | 0 | 0
WHHN03;DC SYS01 | THAMES VALLEY | 2022-10-06 |  | 19.995 | 6.2158 | -34.6161 | -6.3955 | 24.2477 | 7.961 | 86.1828 | 155.129 | 0 | 0 | 0 | 0 | 0 | 1
WKGN01;DC SYS01 | SOUTH | 2022-01-28 |  | 82.0158 | 44.4983 | 72.2165 | 25.3623 | 81.7037 | 43.5729 | 85.2159 | 56.2425 | 0 | RA | 0 | 0 | 0 | 2.4
WONTL1; DC SYS02 | NORTH WEST | 2024-03-05 |  | 88.9908 | 7.275 | 88.902 | 7.2096 | 78.6325 | 3.312 | 85 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0.9
WTNTK1;DC SYS01 | NORTH WEST | 2022-03-25 16:00 |  | 32.6781 | 19.5905 | 4.4463 | 1.878 | 24.3218 | 12.9709 | 42.7525 | 30.1405 | 0 | RA | 0 | 0 | 0 | 2.7
WTT;DC SYS01 | ANGLIA | 2021-02-24 |  | 62.1027 | 13.8741 | 42.9704 | 6.3793 | 59.9215 | 12.6583 | 70.1358 | 19.8835 | 0 | 0 | 0 | 0 | 0 | 1
WVHTF1;DCSys01 | MIDLANDS | 2022-03-07 11:00 |  | 45.8341 | 10.2396 | -7.5759 | -0.8522 | 53.6616 | 14.0134 | -9.018 | -1.001 | 0 | RA | 0 | 0 | 0 | 2.4
YRK;DC SYS01 | NORTH EAST | 2020-08-06 |  | 46.1774 | 12.08 | 28.2365 | 5.54 | 33.3485 | 7.0448 | 57.3333 | 18.92 | 0 | 0 | 0 | 0 | 0 | 1
YRKTH1; DC SYS01 | NORTH EAST | 2022-06-27 09:52 |  | 48.875 | 4.2619 | -0.98765 | -0.0436 | 55.8988 | 5.6507 | 80.1862 | 18.0419 | 0 | 0 | 0 | 0 | 0 | 0
| #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
| #N/A | #N/A | [10 empty] | #N/A | #N/A |  | #N/A | #N/A
[13 empty] | #N/A | #N/A |  | #N/A | #N/A
Formulas:
Over 1 year count since reading = VLOOKUP([Colours Legend],All!A:AM,11,0)
Note on K198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The cooling at site is not an issue, compared against the load for RDGCD1 & CD2

## Site check
Site | Suite sections | Number of cabs |  |  |  | Cells this colour either require a selection to be made, or for a new load to be entered, all other cells will auto fill out.
BHMN05 | 5 |  |  |  |  | If a site is capped all cells will automatically turn this color with white text when you select the site
[5 empty] | Blue text | This is a dual system, use site check - dual for this site
Systems | % Power Remaining (@ 80% of N ) | kW Power Remaining (@ 80% of N ) | % Power Remaining (Inc. Full Batt Recharge) | kW Power Remaining (Inc. Full Batt Recharge) | % Autonomy Remaining | kW Autonomy Remaining | % Cooling Remaining (@ 75% of N) | kW Cooling Remaining (@ 75% of N) | P-Core | RA | PX | Total Allocated Load kW | New load (kW) | Dual/Single | Capped? | Reason
BHMN05;DC SYS A | 63.6477 | 58.9086 | 60.2429 | 50.9821 | 30.0053 | 14.4231 | 59.2176 | 48.8545 | 0 | 0 | 0 | 1 |  | Dual | Capped | Space
BHMN05;DC SYS B | 59.0547 | 54.6576 | 54.3375 | 45.0961 | 28.9402 | 15.4339 | 54.0648 | 44.6035 | 0 | 0 | 0 | 1 |  | Dual | Capped | Space
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A
Distribution | System | Site | Existing Load A | Existing Load B | Reading Date | Max A | Max B | Pairs of breakers spare | [6 empty] | Updated including allocated
[8 empty] | 100 | 80 | 63 | 40 | 20 | Spare positions | Potential new load | Load A | Load B | Max A | Max B | 90% Max | 75% Max | >75%
BHMN05_SEC_DCDB_AG01 | BHMN05;DC SYS A | BHMN05 | 260 | 280 | 2023-02-01 | 300 | 300 | 0 | 0 | 0 | 5 | 6 | 0 | 0 | 0 | 0 | 300 | 300 | 270 | 225 | 224.97
BHMN05_SEC_WALL_DCDB_A | BHMN05;DC SYS A | BHMN05 | 120 | 120 | 2023-02-01 | 200 | 200 | 4 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 200 | 200 | 180 | 150 | 149.98
BHMN05_SEC_WALL_DCDB_B | BHMN05;DC SYS A | BHMN05 | 95 | 95 | 2023-02-01 | 200 | 200 | 6 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 200 | 200 | 180 | 150 | 149.98
BHMN05_SEC_WALL_DCDB_C | BHMN05;DC SYS A | BHMN05 | 90 | 105 | 2023-02-01 | 200 | 200 | 6 | 1 | 0 | 1 | 2 | 0 | 0 | 2 | 41.6667 | 200 | 200 | 180 | 150 | 149.98
BHMN05_SEC_WALL_DCDB_D | BHMN05;DC SYS A | BHMN05 | 100 | 120 | 2023-02-01 | 200 | 200 | 0 | 1 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 200 | 200 | 180 | 150 | 149.98
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Formulas:
Reading Date = VLOOKUP([Site],'DC Dist Allocations'!$A:$X,7,0)

## SYS Allocations
Colours Legend |  |  | Reading calculator
Multiple Single Systems |  |  | 441 | A |  | 24.0345 | kW | Red text | for provisional loads to be discussed
True A & B Systems | [7 empty] | Cell comments | Add for load readings etc, if new updated add as a reply on existing comment
True A & B Systems
BRAG <0 = BLACK 0 - 10 = RED 10 - 25 = AMBER >25 = GREEN | P-Core | RA | PX | Amitie | Op-Ex | Total Allocated Load kW | Total Allocated Load A | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW | Cab ID + equipment + [Initials] e.g. A01 7210 [DF] | Allocated Load kW Sheet2
ABH;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
ABN;DC SYS01 | [5 empty] | 6.5 | 119.2661 | B03a Nokia 7210 | 0.5 | Ciena 6500-14 - G1 | 2 | Ciena 6500-14 - H1 | 2 | Ciena 6500-14 - E1 | 2 | [31 empty] | 0
ABNTB1;DC SYS01 | [5 empty] | 2 | 36.6972 | 6500-14 B09 | 1 | EF1e Alcatel 7210 | 1 | [35 empty] | 0
ABNTD1;DCSYS01 | [5 empty] | 5 | 91.7431 | 6500-14 E01 | 4 | CD04 Alcatel 7210 | 1 | [35 empty] | 0
ACTN01;DC SYS01a |  | RA |  |  | OPEX | 6.85 | 125.6881 | AS/AT19 RA | 1.3 | AS/AT13-17 Op-Ex | 2.95 | ASAT11 Alcatel 7210 | 0.8 | ASAT12 Alcatel 7210 | 0.8 | AL08 Cisco ASA-5585 | 0.5 | AG 3a BT EAD | 0.5 | [27 empty] | 0
ACTN01;DC SYS01b | [5 empty] | 5.55 | 101.8349 | AS/AT19 RA | 0.5 | AS/AT13-17 Op-Ex | 2.25 | ASAT11 Alcatel 7210 | 0.8 | ASAT12 Alcatel 7210 | 1 | AL08 Cisco ASA-5585 | 0.5 | AG 3a BT EAD | 0.5 | [27 empty] | 0
ANSTW1; DC SYS01 | [5 empty] | 0.4 | 7.3394 | A04 Ciena 6500-7 slot | 0.4 | [37 empty] | 0
ASH;DC SYS01 | [5 empty] | 0.5 | 9.1743 | C14 BT EAD | 0.5 | [37 empty] | 0
ASMN02;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
AYRN01; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
AZTCD1&2;DC SYS01 |  | RA |  |  |  | 6.9 | 126.6055 | HJ01 RA | 2.4 | L08 Nokia1830 | 0.5 | LM04 Alcatel 7210 | 2 | TU08 Alcatel 7210 | 1 | NP07 BT EAD | 1 | [29 empty] | 0
BCT;DC SYS01 | [5 empty] | 2 | 36.6972 | J02 6500-14 | 2 | [37 empty] | 0
BDEN02;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
BDEN06;DC SYS01 | [5 empty] | 5.5 | 100.9174 | E05 6500-14 | 2 | A3 Ciena RLS R4 | 2 | AB4 Ciena Waveserver 5 | 1.5 | [33 empty] | 0
BDFN02;DC SYS01a | P-Core | RA | PX |  | OPEX | 12.55 | 230.2752 | BD08 PE7750 | 2 | BF06 PX | 0.3 | BF08 RA | 1.2 | BF03 WS&RLS | 1.45 | BF04 WS&RLS | 1.15 | BF05 WS&RLS | 1.75 | BB01 BT EAD | 1 | BD08 WS 5 | 2.2 | AL02 Nokia ESA400 | 1.5 | [21 empty] | 0
BDFN02;DC SYS01b | [5 empty] | 11.65 | 213.7615 | BD08 PE7750 | 2 | BF06 PX | 0.4 | BF08 RA | 0.4 | BF03 WS&RLS | 1.45 | BF04 WS&RLS | 0.95 | BF05 WS&RLS | 1.75 | BB01 BT EAD | 1 | BD08 WS 5 | 2.3 | AL02 Nokia ESA401 | 1.4 | [21 empty] | 0
BFDTB1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
BFEC01;DC SYS01 |  | RA |  |  |  | 18.4 | 337.6147 | C/CC04 RA | 2.4 | C/CC 03 Alcatel 7210 | 1 | B11 6500&SAS SX | 5 | B8 RLS & Waveserver | 5 | B9 RLS & Waveserver | 5 | [29 empty] | 0
BFTN03;DC SYS01 |  | RA |  |  |  | 14.2 | 260.5505 | BC03 RA | 1.7 | D04 6500-14 | 2 | 2 x 6500-14 B08 | 1 | BC04 Alcatel 7210 | 1 | L07 RLS& Waveserver | 2.5 | L08 RLS& Waveserver | 2.5 | L06 IGW | 3.5 | [25 empty] | 0
BHM;DC SYS02 | P-Core |  |  |  |  | 0 | 0 | [39 empty] | 0
BHMN05;DC SYS A | [5 empty] | 1 | 18.3486 | ANAP1 Alcatel 7210 | 1 | [37 empty] | 0
BHMN05;DC SYS B | [5 empty] | 1 | 18.3486 | ANAP1 Alcatel 7210 | 1 | [37 empty] | 0
BHMN08;DCSYS03A |  | RA | PX |  | OPEX | 7.85 | 144.0367 | D2 PX | 0.3 | D3 RA | 1.2 | D5 Util | 0.9 | C2 Op-Ex | 1.55 | C3 Op-Ex | 0.8 | C5 Op-Ex | 1.3 | C06 WS5 & ai | 1.8 | [25 empty] | 0
BHMN08;DCSYS03B | [5 empty] | 8.28 | 151.9266 | D2 PX | 0.5 | D3 RA | 1.4 | D5 Util | 0.93 | C2 Op-Ex | 1.55 | C3 Op-Ex | 0.8 | C5 Op-Ex | 1.3 | C06 WS5 & ai | 1.8 | [25 empty] | 0
BHMTF1;DC SYS A |  | RA |  |  |  | 2.4 | 44.0367 | AB01 RA | 2.4 | [37 empty] | 0
BHMTF1;DC SYS B | [5 empty] | 2.5 | 45.8716 | AB01 RA | 2.5 | [37 empty] | 0
BHWCN1;DC SYS01 | [5 empty] | 1 | 18.3486 | B05 MSP7750 PE | 1 | [37 empty] | 0
BIFTS1; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
BKBN41;DC SYS01 | [5 empty] | 3 | 55.0459 | E05 6500-14 | 1 | Ciena 6500-14 BC06 | 2 | [35 empty] | 0
BKLN05;DC SYS02 | P-Core |  |  |  |  | 37.8 | 693.578 | Inverter Load | 19 | Facebook BQBR09 | 2 | Netflix BNBP12 | 2.9 | Google BLBM14 | 3.9 | AKAMAI BL13 | 5 | AKAMAI BE09 | 5 | [27 empty] | 0
BKLN05;DC SYS03;NEAR CK | P-Core |  |  |  |  | 21 | 385.3211 | Inverter Load | 19 | IGW BNBP7 | 2 | [35 empty] | 0
BKLN05;DC SYS04a | P-Core | RA | PX |  | OPEX | 62.65 | 1149.5413 | VSS DC&DF1,2,4 | 17.1 | Group DE/DD | 26.75 | DG1 RA | 1 | DG2 PX | 0.4 | DG4 Op-Ex | 0.35 | DG5 Op-Ex | 0.5 | DG6 Op-Ex | 0.45 | DG8 M-PE | 0.225 | DG9 M-PE | 0.225 | DF8 IGW+WSaI | 0.7 | DF9 7750 SR7s | 0.5 | DF10 Utility Cab | 0.95 | ACAD04 Alcatel 7210 | 1 | ACAD05 Alcatel 7210 | 1 | ACAD06 Alcatel 7210 | 1 | DC10 DALI | 6.05 | BE08 QWILT | 2 | BN14 SKY/AKAMAI | 2.45 |  |  |  | 0
BKLN05;DC SYS04b | [5 empty] | 62.65 | 1149.5413 | VSS DC&DF1,2,4 | 17.1 | Group DE/DD | 26.75 | DG1 RA | 1 | DG2 PX | 0.4 | DG4 Op-Ex | 0.35 | DG5 Op-Ex | 0.5 | DG6 Op-Ex | 0.45 | DG8 M-PE | 0.225 | DG9 M-PE | 0.225 | DF8 IGW+WSaI | 0.7 | DF9 7750 SR7s | 0.5 | DF10 Utility Cab | 0.95 | ACAD04 Alcatel 7210 | 1 | ACAD05 Alcatel 7210 | 1 | ACAD06 Alcatel 7210 | 1 | DC10 DALI | 6.05 | BE08 QWILT | 2 | BN14 SKY/AKAMAI | 2.45 |  |  |  | 0
BMGV03; DC SYS A | [5 empty] | 0 | 0 | [39 empty] | 0
BMGV03; DC SYS B | [5 empty] | 0 | 0 | [39 empty] | 0
BMTDN1;DC SYS01 | [5 empty] | 0.5 | 9.1743 | DE05 BT UTILITY | 0.5 | [37 empty] | 0
BPL;DC SYS01 | [5 empty] | 5.4 | 99.0826 | G04 CPL | 1 | DE4 UTILITY RACK | 4.4 | [35 empty] | 0
BRETS1;DC SYS01 | [5 empty] | 0.5 | 9.1743 | Ciena 6500 7Slot D04 | 0.5 | [37 empty] | 0
BRRTS1; DC SYS01 | [5 empty] | 0.4 | 7.3394 | A02 Ciena 6500-7 slot | 0.4 | [37 empty] | 0
BSG;DC SYS01 | [5 empty] | 4 | 73.3945 | FG15 Alcatel 7210 | 3 | FG16 ADVA XG120 | 1 | [35 empty] | 0
BSH;DC SYS01;GND | P-Core | RA | PX |  |  | 20.8 | 381.6514 | A2 RA | 0.5 | A3 PX | 0.2 | B2 Op-Ex | 1.5 | B3 Op-Ex | 1.4 | B5 Op-Ex | 1.3 | B6 Op-Ex | 1.4 | B7 Util rack | 0.7 | A6 IGW+Wsai | 1 | A7 Netflix | 1.1 | Sky | 2 | HomeBB DNS B7 | 2.2 | WS5 | 4 | A10 Nokia 7750SR7s | 1.1 | A9 QWILT | 2 | A4 Cisco | 0.4 | [9 empty] | 0
BSH;DC SYS02;GND | P-Core |  |  |  |  | 23.3 | 427.5229 | A2 RA | 1.7 | A3 PX | 0.5 | B2 Op-Ex | 1.5 | B3 Op-Ex | 1.3 | B5 Op-Ex | 1.3 | B6 Op-Ex | 1.5 | B7 Util rack | 0.7 | A6 IGW+Wsai | 0.7 | A7 Netflix | 1.1 | Sky | 2 | HomeBB DNS B7 | 2.2 | WS5 | 4 | A10 Nokia 7750SR7s | 1.2 | A9 QWILT | 2 | A4 Cisco | 0.4 | MSPP | 1.2 | [7 empty] | 0
BSH;DC SYS03;GND | P-Core |  |  |  |  | 3.6 | 66.055 | E9 - Facebook | 0.8 | E10 - Facebook | 1 | Google | 1.8 | [33 empty] | 0
BSHN03;DC SYS A | [5 empty] | 16.6 | 304.5872 | CA17 6500-7 | 2 | CC12 6500-14 | 2 | Load Transfer | 8.7 | MSPP | 0.6 | Virgin media NTE BH18 | 1.1 | Cisco 6300 C02 | 1.1 | Cisco 6300 C04 | 1.1 | [25 empty] | 0
BSHN03;DC SYS B | [5 empty] | 14.6 | 267.8899 |  |  | CC12 6500-14 | 2 | Load Transfer | 8.7 | MSPP | 0.6 | Virgin media NTE BH18 | 1.1 | Cisco 6300 C02 | 1.1 | Cisco 6300 C04 | 1.1 | [25 empty] | 0
BTFTB1;DC SYS01 | P-Core |  |  |  |  | 0 | 0 | [39 empty] | 0
BTFTB1;DC SYS02 |  | RA | PX |  | OPEX | 32.45 | 595.4128 | AA02 RA | 2.5 | S27 PX | 1 | AA07 Netflix | 1.8 | AA06 Akamai | 1.3 | AB02-06 Op-Ex | 10.9 | A03 BT EAD | 0.5 | AA9 BNG | 1.8 | AA3 Facebook | 2.65 |  |  | AZ10 Alcatel 7210 | 2 | AB 7 QWILT | 2.4 | AA10 Google | 2.2 | IGW NCS-57C3 | 0.5 | Nokia ESA400 AA11 | 2.9 | [11 empty] | 0
BTLCD1;DC SYS01 | [5 empty] | 2.25 | 41.2844 | Nokia 1830 ILA | 2 | BC09 BT ADVA | 0.25 | [35 empty] | 0
BTLN08;DC SYS01 | P-Core |  |  |  |  | 5 | 91.7431 | CG05 Nokia 1830 | 2 | CTCU4 Alcatel 7210 | 3 | [35 empty] | 0
BTLN09;DC SYS01 |  | RA | PX | AM | OPEX | 48.13 | 883.1193 | A02 RA | 1.8 | A04 PX | 1.2 | B02 to 5 Opex | 4.7 | B08 Akamai | 1.9 | B07 IGW | 1.8 | C11 to 26 Amitie | 11.7 | B10 BNG | 1.9 | A7 Facebook | 2.3 | A10 Google | 1.2 | Broadband Capacity | 0.5 | A11 QWILT | 6 | B24 Ciena6500 R8 | 1.7 | B13 Nokia SEGGW ESA400 | 2.9 | A5 Utility | 0.93 | B22 Waverserver_5 | 2 | A8 Facebook | 5.6 | [7 empty] | 0
BTN-DCSYS01 |  | RA |  |  |  | 2.7 | 49.5413 | YZ02 RA | 1.7 | YZ04 Alcatel 7210 | 1 | [35 empty] | 0
BTNW01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
BTRTP1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
BYR;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CAMN02;DC SYS01 | [5 empty] | 1 | 18.3486 | DE09 Alcatel 7210 | 1 | [37 empty] | 0
CAMN41;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CBY;DC SYS01 | [5 empty] | 1 | 18.3486 | JK08 Alcatel 7210 | 1 | [37 empty] | 0
CDFN02;DC SYS01 | [5 empty] | 3 | 55.0459 | C05 Nokia 1830 | 0.5 | GH5 7210 SAS SX | 2.5 | [35 empty] | 0
CELL01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CFDTN1;DC SYS01 | [5 empty] | 1.5 | 27.5229 | JK04 DCN | 0.5 | G06 Ciena 5171 | 1 | [35 empty] | 0
CHDCD1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CHMN21;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CHTN07;DC SYS01 | P-Core |  |  |  |  | 15.5 | 284.4037 | BT EAD AMAN07 | 1 | BT EAD ST04 | 1 | EF03 Alcatel 7210 | 2 | EF04 Alcatel 7210 | 2 | EF05 Alcatel 7210 | 2 | EF07 Alcatel 7210 | 2 | Ciena 6500 AA AB 02 | 1.1 | NOKIA 7250 A5 | 2.2 | NOKIA 7250 A6 | 2.2 | [21 empty] | 0
CHTN07;DC SYS02 | P-Core |  |  |  |  | 1.5 | 27.5229 | 7750 12B AN10 | 1.5 | [37 empty] | 0
CHTTN3;DC SYS01A |  | RA | PX |  | OPEX | 7.8 | 143.1193 |  |  | BD09 RA | 0.4 | BD06 Op-Ex | 1.45 | BD05 Op-Ex | 0.45 | BD04 Op-Ex | 1.15 | BE9 7750 SR7s | 0.35 | WS5 | 4 | [25 empty] | 0
CHTTN3;DC SYS01B | [5 empty] | 8.4 | 154.1284 |  |  | BD09 RA | 0.9 | BD06 Op-Ex | 1.35 | BD05 Op-Ex | 0.45 | BD04 Op-Ex | 1.15 | BE9 7750 SR7s | 0.55 | WS5 | 4 | [25 empty] | 0
CKNN03-DCSYS01a |  |  |  | AM |  | 6.9 | 126.6055 | E&F 1-6 Amitie | 5.9 | CD5 Ciena 6500 R8 | 1 | [35 empty] | 0
CKNN03-DCSYS01b | [5 empty] | 6.8 | 124.7706 | E&F 1-6 Amitie | 5.8 | CD5 Ciena 6500 R8 | 1 | [35 empty] | 0
COV;DC SYS01a |  |  |  |  | OPEX | 9.35 | 171.5596 | AB04 Opex | 2.25 | AB05 Opex | 2.25 | AB06 Opex | 2.25 | EF1 Alcatel 7210 | 1 | AJ05 Cisco ASA-5585 | 0.5 | P0 BT EAD | 1.1 | [27 empty] | 0
COV;DC SYS01b | [5 empty] | 9.35 | 171.5596 | AB04 Opex | 2.25 | AB05 Opex | 2.25 | AB06 Opex | 2.25 | EF1 Alcatel 7210 | 1 | AJ05 Cisco ASA-5585 | 0.5 | P0 BT EAD | 1.1 | [27 empty] | 0
COWL02;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CSLN13;DC SYS01 | [5 empty] | 1 | 18.3486 | Ciena 6500 14 D05 | 1 | [37 empty] | 0
CTNN01-DCSYS01a |  |  |  | AM |  | 6.8 | 124.7706 | S&T 1-6 Amitie | 5.8 | CD01 Ciena 6500 R8 | 1 | [35 empty] | 0
CTNN01-DCSYS01b | [5 empty] | 6.9 | 126.6055 | S&T 1-6 Amitie | 5.9 | CD01 Ciena 6500 R8 | 1 | [35 empty] | 0
CTRTK1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
CTRTS1; DC SYS01 |  | RA |  |  |  | 4 | 73.3945 | EF10 RA | 3 | IJ08 Alcatel 7210 | 1 | [35 empty] | 0
CYNTN2;DC SYS01 | [5 empty] | 3 | 55.0459 | E10 BT EAD | 2 | BA05 Alcatel 7210 | 1 | [35 empty] | 0
DBY;DC SYS01 | [5 empty] | 1 | 18.3486 |  |  | TU01 Alcatel 7210 | 1 | [35 empty] | 0
DCT;DC SYS01 | [5 empty] | 4.4 | 80.7339 | Alcatel & Ciena Y2 | 4.4 | [37 empty] | 0
DFSN01; DC SYS01 | [5 empty] | 1 | 18.3486 |  |  | BT OSA AB08 | 1 | [35 empty] | 0
DFSNC1; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DGS;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DHMNU1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DKTN08; DC SYS01 |  | RA |  |  |  | 7.4 | 135.7798 | ST04 RA | 2.4 | ST05 Alcatel 7210 | 2 | ST07 Alcate 7210 | 2 | A04 BT EAD | 1 | [31 empty] | 0
DLD;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DLNTC1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DNDN71; SYS 01 |  | RA |  |  |  | 4.7 | 86.2385 | DE06 RA | 1.7 | A04 6500-14 | 2 |  |  |  |  | Marconi MSPP 1684 C04 | 1 | [29 empty] | 0
DNDTC1;DCSYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DNFNP1; DC SYS01 | [5 empty] | 0.5 | 9.1743 | B03 Ciena 6500-7 | 0.5 | [37 empty] | 0
DONTN1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DVSTB1; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
DWLTM1;DC SYS01 | [5 empty] | 4 | 73.3945 | A03 CIENA 6500-14 SLOT | 4 | [37 empty] | 0
ECBTC1; DC SYS01 | [5 empty] | 1 | 18.3486 | A7 Ciena 6500 | 1 | [37 empty] | 0
EDBCD1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
EDBTG1;DC SYSA |  | RA | PX |  | OPEX | 22.55 | 413.7615 | BA02 RA | 1.4 | BA03 PX | 0.6 | BB02 Op-EX | 1.3 | BB03 Op-Ex | 1.5 | BA05 Alcatel 7210 | 0.3 | BB04 IGW | 1.8 | BA06 QWILT | 1.7 | CDN Move |  | BA7 Akami | 2.75 | BA9 FACEBOOK | 2.75 | BA10 FACEBOOK | 2.75 | BA11 Google | 0.7 | BB11 Nokia SecGW | 2 | BB10 Nokia SecGW ESA400 | 2 | BB9 Nokia RR & Cisco RR | 1 | [9 empty] | 0
EDBTG1;DC SYSB | [5 empty] | 22.05 | 404.5872 | BA02 RA | 0.6 | BA03 PX | 0.5 | BB02 Op-EX | 1.2 | BB03 Op-Ex | 1.4 | BA05 Alcatel 7210 | 0.3 | BB04 IGW | 1.8 | BA06 QWILT | 1.8 | CDN Move |  | BA7 Akami | 2.75 | BA9 FACEBOOK | 2.75 | BA10 FACEBOOK | 2.75 | BA11 Google | 1.2 | BB11 Nokia SecGW | 2 | BB10 Nokia SecGW ESA400 | 2 | BB9 Nokia RR & Cisco RR | 1 | [9 empty] | 0
EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | P-Core |  |  |  |  | 7.7515 | 142.2294 | JK03 DL360 | 1 | A02 Op-EX | 2.3 | Google | 0.9 | Netflix | 1.5 | AB05 Alcatel 7210 | 1 | QWILT | 0.3015 | Broadband Capacity | 0.25 | Security & Misc XY1 | 0.5 | [23 empty] | 0
EDBTN1;DC SYSB | [5 empty] | 7.7515 | 142.2294 | JK03 DL361 | 1 | A02 Op-EX | 2.3 | Google | 0.9 | Netflix | 1.5 | AB05 Alcatel 7210 | 1 | QWILT | 0.3015 | Broadband Capacity | 0.25 | Security & Misc XY1 | 0.5 | [23 empty] | 0
EGNTM1;DC SYS01 | [5 empty] | 1 | 18.3486 | A02 Ciena 6500 - 7 Slot | 1 | [37 empty] | 0
EVMN01;DC SYS01 | [5 empty] | 1 | 18.3486 | AB02 XG210 | 1 | [37 empty] | 0
EXR;DC SYS01 | [5 empty] | 3 | 55.0459 | PN02 Utility Cab | 2 | LM06 BT OSA NTE | 1 | [35 empty] | 0
EXRN03-DCSYSa |  |  |  | AM |  | 5.9 | 108.2569 | J&K 1-6 Amitie | 5.9 | [37 empty] | 0
EXRN03-DCSYSb | [5 empty] | 5.8 | 106.422 | J&K 1-6 Amitie | 5.8 | [37 empty] | 0
FKE;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
FLNTT1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
FMYN31; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
FRNN03-DCSYS01a |  |  |  | AM |  | 5.9 | 108.2569 | G&H 1-6 Amitie | 5.9 | [37 empty] | 0
FRNN03-DCSYS01b | [5 empty] | 5.8 | 106.422 | G&H 1-6 Amitie | 5.8 | [37 empty] | 0
GCRTB1;DC SYS01 |  | RA |  |  |  | 3.9 | 71.5596 | B18 RA | 2.4 | AB30a CIENA 5171 | 1 | ADVA XG120 H7 | 0.5 | [33 empty] | 0
GFDCD1;DC SYS01A |  | RA |  |  |  | 7.3 | 133.945 | HH/HJ 10 Wsai | 2.2 | HH/HJ 11 Wsai | 2.4 | HH/HJ09 RA | 1.5 | AE01 Alcatel 7210 | 0.8 | HH/JJ08 BT OSA | 0.4 | [29 empty] | 0
GFDCD1;DC SYS01B | [5 empty] | 6.6 | 121.1009 | HH/HJ 10 Wsai | 2.1 | HH/HJ 11 Wsai | 2.3 | HH/HJ09 RA | 1.1 | AE01 Alcatel 7210 | 0.8 | HH/JJ08 BT OSA | 0.3 | [29 empty] | 0
GLWN07;DC SYS A | P-Core | RA | PX |  | OPEX | 11.75 | 215.5963 | J22 PX | 0.75 | CD25 Opex | 1.2 | CD26 Opex | 1.4 | CD22 RA | 0.3 | Alcatel 7210 CD29 | 0.9 | CD27 Alcatel 7210 | 0.8 | CD30 Ciena 6500 | 1.6 | CD23 PX | 0.5 | RLS & WAVESERVER AA22 | 2 | WAVESERVER 5 AA23 | 2.3 | [19 empty] | 0
GLWN07;DC SYS B | [5 empty] | 13.95 | 255.9633 | J22 PX | 0.75 | CD25 Opex | 1.3 | CD26 Opex | 1.5 | CD22 RA | 1.8 | Alcatel 7210 CD29 | 0.9 | CD27 Alcatel 7211 | 0.7 | CD30 Ciena 6500 | 1.9 | CD23 PX | 0.7 | RLS & WAVESERVER AA22 | 2.1 | WAVESERVER 5 AA23 | 2.3 | [19 empty] | 0
GLWTO1;DC SYS01 |  | RA |  |  |  | 4.4 | 80.7339 | KL06 RA | 2.4 | LK07 Alcatel 7210 | 2 | [35 empty] | 0
GLWTW1;DC SYS01 | [5 empty] | 3 | 55.0459 | GH11 Alcatel 7210 | 2 | CD03 Cisco ISR 4331 | 1 | [35 empty] | 0
GRSTB1;DC SYS01 | [5 empty] | 2.7 | 49.5413 | A04 Ciena 6500-7 | 0.5 | A06 MSPP 1684 | 2.2 | [35 empty] | 0
GWK;DC SYS01 | [5 empty] | 0.5 | 9.1743 | LO1 BT Utility | 0.5 | [37 empty] | 0
HHD;DC SYS01 | [5 empty] | 2 | 36.6972 | CD02 ALCATEL 7210 SAS SX | 1 | CD08 BT EAD | 1 | [35 empty] | 0
HLDA11;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
HLDA12;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
HLWN02;DC SYS01 | [5 empty] | 1 | 18.3486 | AB04 Alcatel 7210 | 1 | [37 empty] | 0
HRWN02;DC SYS01 |  | RA |  |  |  | 5.9 | 108.2569 | KJ03 RA | 2.4 | G14 BT EAD | 2 | JK04 Alcatel 7210 | 1 | C03 BT EAD[KA7] | 0.5 |  |  | C03 BT EAD[KA7] | [28 empty] | 0
HTE;DC SYS01 | [5 empty] | 1 | 18.3486 | CD05 Ciena 6500 | 1 | [37 empty] | 0
IGNN01;DC SYS01 |  | RA |  |  |  | 4.4 | 80.7339 | JK14 RA | 2.4 | JK13 7210 | 1 | GH17 Alcatel 7210 | 1 | [33 empty] | 0
INVN41;DC SYS01 |  | RA |  |  |  | 6.4 | 117.4312 | EF04 RA | 2.4 | C03 Ciena 6500-14 SLOT | 4 | [35 empty] | 0
INVTL1;DC SYS01 | [5 empty] | 4 | 73.3945 | C08 Ciena 6500-14 SLOT | 4 | [37 empty] | 0
IODN01;DC SYS01 |  | RA |  |  | OPEX | 10.4 | 190.8257 | HJ05 RA | 2.4 | HJ08 Opex | 2 | MN01 BT EAD | 1 | MN02 RLS& WSai | 5 | [31 empty] | 0
IODTA1;DC SYS01 |  |  |  |  | OPEX | 1 | 18.3486 | AB07 WSai 5 | 1 | [37 empty] | 0
IPWTN1;DC SYS01 |  | RA |  |  |  | 6.7 | 122.9358 | RQ03 RA | 1.7 | BT OSA ORMT_SAP_220412_32_11408314 | 1 | RQ06 CIENA 6500-14 SLOT | 4 | [33 empty] | 0
IVER02; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
KLNN01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
KNLTS1;DC SYS01 | [5 empty] | 0.5 | 9.1743 | K03 Ciena 6500 | 0.5 | [37 empty] | 0
LCT;DC SYS01 |  | RA |  |  |  | 13.5 | 247.7064 | BA02 RA | 1.1 | BA03 MDCN | 4.9 | ST07 Alcatel 7210 | 1 | NP03 Cisco ASA-5585 | 1 | BA4 IGW,BA5 IGW | 5.5 | [29 empty] | 0
LDMS13;DC SYS01 A | [5 empty] | 0 | 0 | [39 empty] | 0
LDMS13;DC SYS01 B | [5 empty] | 0 | 0 | [39 empty] | 0
LDSCD2;DC SYS A | P-Core | RA | PX |  | OPEX | 17.5 | 321.1009 |  |  |  |  | ABAC02-06 Op-Ex | 0.7 | Netflix TU9 | 1.45 | Google TU5 | 0.9 | HomeBB DNS XY05 | 1.5 | AB7 WS5 & ai | 1.8 | VW04 Alcatel 7210 | 0.5 | VW05 Alcatel 7210 | 0.2 | X6 QWILT | 1.7 | Broadband Capacity | 0.25 | CD06 Juniper SRX 4200 | 0.5 | Nokia 7750 SR-7s AB13 | 3 | G15 BT OSA | 1.6 | Facebook TU7 | 2.8 | Facebook TU8 | 0.6 | [7 empty] | 0
LDSCD2;DC SYS B | [5 empty] | 20.7 | 379.8165 | XY2 RA | 2.1 | XY03 PX | 0.4 | ABAC02-06 Op-Ex | 1.4 | Netflix TU9 | 1.45 | Google TU5 | 0.9 | HomeBB DNS XY05 | 1.5 | AB7 WS5 & ai | 1.8 | VW04 Alcatel 7210 | 0.5 | VW05 Alcatel 7210 | 0.2 | X6 QWILT | 1.7 | Broadband Capacity | 0.25 | CD06 Juniper SRX 4200 | 0.5 | Nokia 7750 SR-7s AB13 | 3 | G15 BT OSA | 1.6 | Facebook TU7 | 2.8 | Facebook TU8 | 0.6 | [7 empty] | 0
LDSN14; DC SYS01 | [5 empty] | 0.1 | 1.8349 | NRA34 Ciena 5142 | 0.1 | [37 empty] | 0
LDSTS1;DC SYS01 |  | RA |  |  |  | 8.1 | 148.6239 | H19 RA | 2.4 | PQ11 Ciena 6500 | 1.5 | P03 BT OSA | 3.2 | H20 Alcatel 7210 | 1 | [31 empty] | 0
LIVN01;DC SYS01 | [5 empty] | 2 | 36.6972 | ASAT02 Alcatel 7210 | 2 | [37 empty] | 0
LLDTE1;DC SYS01 |  | RA |  |  |  | 5.9 | 108.2569 | PQ09 RA | 2.4 | Ciena 6500 N08 | 3.5 | [35 empty] | 0
LMSCN2;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
LPLTB1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
LPLTK1;DC SYS01 |  | RA |  |  |  | 1.7 | 31.1927 | A06 RA | 1.7 | [37 empty] | 0
LSWN01;DC SYS01 | [5 empty] | 11.5 | 211.0092 | RS07 Polatis | 2 | RS08 Polatis | 2 | GF06 Alcatel7210 SAS X | 1 | DE09 Alcatel 7210 | 1 | WACS CoLo |  | F03 Ciena 6500-14 slot | 5.5 | [27 empty] | 0
LTNDN1;DC SYS01 | [5 empty] | 1 | 18.3486 | DE07 Alcatel 7210 | 1 | [37 empty] | 0
MCRCD2;DC SYS01 [Rect1&2] | [5 empty] | 2 | 36.6972 | T06 Ciena 5142 | 2 | [37 empty] | 0
MCRCD2;DC SYS02 [Rect 3&4] |  | RA | PX |  | OPEX | 19.1 | 350.4587 | T6 WS5 & ai | 3.6 | VW2 RA | 1.8 |  |  | TU2 Op-Ex | 2.2 | TU3 Op-Ex | 2 | TU5 Op-Ex | 2.2 | NOKIA SEGW V6 | 2.3 | V05 DCN | 0.8 | T07 RLS & Waveserver | 4.2 | [21 empty] | 0
MCRCD2;DC SYS03 [Rect5] | [5 empty] | 0 | 0 | [39 empty] | 0
MCRN11;DC SYS01a | P-Core |  |  |  |  | 4 | 73.3945 | KL14 Alcatel 7210 | 2 | KL15 Alcatel 7210 | 2 | [35 empty] | 0
MCRN11;DC SYS01b | [5 empty] | 0 | 0 | [39 empty] | 0
MCRN12;DC SYS01 A | P-Core | RA | PX |  | OPEX | 18.625 | 341.7431 | CC04,6&7Op-ex | 2.6 | CC10 RA | 0.9 |  |  | AB05 BT EAD | 0.125 | CH01 IGW+WSaI | 0.6 | CF5Facebook | 0.75 | CF2 Netflix | 0.85 | CF4 Akamai | 0.75 | CF1 Google | 0.5 | CH2 7750 SR7s | 0.35 | CE1 AWS | 1.4 | CCCD2 WS5 | 1.8 | CE2 QWILT | 2.15 | cc03 SECGW | 1.1 | BJ03 Alcatel 7210 SAS SX | 0.8 | BJ05 Alcatel 7210 SAS SX | 0.8 | BJ06 Alcatel 7210 SAS SX | 0.8 | CH08 AWS | 1.5 | CF6Facebook | 0.85 |  | 0
MCRN12;DC SYS01 B | [5 empty] | 18.225 | 334.4037 | CC04,6&7Op-ex | 2.4 | CC10 RA | 0.5 |  |  | AB05 BT EAD | 0.125 | CH01 IGW+WSaI | 0.6 | CF5Facebook | 0.85 | CF2 Netflix | 0.85 | CF4 Akamai | 0.85 | CF1 Google | 0.4 | CH2 7750 SR7s | 0.45 | CE1 AWS | 1.4 | CCCD2 WS5 | 1.8 | CE2 QWILT | 2.05 | CC03 SECGW | 1.2 | BJ03 Alcatel 7210 SAS SX | 0.8 | BJ05 Alcatel 7210 SAS SX | 0.8 | BJ06 Alcatel 7210 SAS SX | 0.8 | CH08 AWS | 1.5 | CF6Facebook | 0.85 |  | 0
MDBTD1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
MDE;DC SYS01 | [5 empty] | 0.3 | 5.5046 | E10 ADVA XG210 | 0.3 | [37 empty] | 0
MDFTB1;DC SYS01 | [5 empty] | 4 | 73.3945 | C05 CIENA 6500 - 14 SLOT | 4 | [37 empty] | 0
MKSTN1;DC SYS01 | [5 empty] | 1 | 18.3486 | QR01 Alcatel 7210 | 1 | [37 empty] | 0
NBYCD1;DC SYS01 | [5 empty] | 0.5 | 9.1743 | Nokia ILA E04 | 0.5 | [37 empty] | 0
NECCD1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
NGM;DC SYS03 | [5 empty] | 1 | 18.3486 | LLMM01 Alcatel 7210 | 1 | [37 empty] | 0
NGMTL1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
NRWN51;DC SYS01 |  | RA |  |  |  | 2.4 | 44.0367 | BC07 RA | 2.4 | [37 empty] | 0
NRWTN1;DC SYS01 | [5 empty] | 1 | 18.3486 | LM01 Alcatel 7210 | 1 | [37 empty] | 0
NULTB1;DC SYS01 |  | RA |  |  |  | 1.7 | 31.1927 | AB05 RA | 1.7 | [37 empty] | 0
NWCN05;DC SYS01a |  | RA |  |  | OPEX | 10.1 | 185.3211 | M01 RA | 0.4 | P01-03 Op Ex | 5.1 | MN02 Alcatel 7210 | 0.8 | E15 IGW | 1.4 | K02, XG210 | 0.5 | Ciena 14Slot - B4 | 0.5 | E13 IGW | 1.4 | [25 empty] | 0
NWCN05;DC SYS01b | [5 empty] | 11.2 | 205.5046 | M01 RA | 1.4 | P01-03 Op Ex | 5.15 | MN02 Alcatel 7210 | 0.85 | E15 IGW | 1.4 | K02, XG210 | 0.5 | Ciena 14Slot - B4 | 0.5 | E13 IGW | 1.4 | [25 empty] | 0
NWCNY1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
NWPDN1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
OHB;DC SYS01;PSU1 | [5 empty] | 2 | 36.6972 | J04 Nokia 1830 | 2 | [37 empty] | 0
OHB;DC SYS02;PSU2 | [5 empty] | 0 | 0 | [39 empty] | 0
OKNN01-DCSYS01a |  | RA |  | AM |  | 7 | 128.4404 | G06 RA | 1 | J&K 1-6 Amitie | 6 | [35 empty] | 0
OKNN01-DCSYS01b | [5 empty] | 7.4 | 135.7798 | G06 RA | 1.5 | J&K 1-6 Amitie | 5.9 | [35 empty] | 0
PCOTN1;DC SYS A;FLAG | [5 empty] | 2 | 36.6972 | AC03 6500-7 | 2 | [37 empty] | 0
PCOTN1;DC SYS A;GEMINI | [5 empty] | 2 | 36.6972 | TU07 Polatis | 2 | [37 empty] | 0
PCOTN1;DC SYS B;FLAG | [5 empty] | 0 | 0 | [39 empty] | 0
PCOTN1;DC SYS B;GEMINI | [5 empty] | 0 | 0 | [39 empty] | 0
PLY-DCSYS01a |  | RA |  | AM |  | 11.8 | 216.5138 | S02 RA | 2.1 | W&X 1-6 Amitie | 5.9 | ST03 Utility Cab | 1.8 | EF09 BT NTE | 1 | U7 Ciena 6500 R8 | 1 | [29 empty] | 0
PLY-DCSYS01b | [5 empty] | 12.5 | 229.3578 | S02 RA | 2.5 | W&X 1-6 Amitie | 6 | ST03 Utility Cab | 2 | EF09 BT NTE | 1 | U7 Ciena 6500 R8 | 1 | [29 empty] | 0
PNRTN1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
POLN02-DCSYS01a |  | RA |  | AM |  | 10.15 | 186.2385 | EF13 BT EAD | 1.25 | J&K 1-6 Amitie | 5.7 | E12 Ciena 6500 R8 | 1 | E14 NOKIA 7750 SR12E(RA) | 1.3 | EF10 Alcatel 7210 | 0.9 | [29 empty] | 0
POLN02-DCSYS01b | [5 empty] | 10.45 | 191.7431 | EF13 BT EAD | 1.25 | J&K 1-6 Amitie | 6 | E12 Ciena 6500 R8 | 1 | E14 NOKIA 7750 SR12E(RA) | 1.3 | EF10 Alcatel 7210 | 0.9 | [29 empty] | 0
PRDTB1;DC SYS01 | [5 empty] | 1 | 18.3486 | A03 CIENA 6500- 7 SLOT | 1 | [37 empty] | 0
PRLN02;DC SYS01 | [5 empty] | 5.4 | 99.0826 | E03 AWS | 4 | E4 Utility Cab | 1.4 | [35 empty] | 0
PTBTN1;DC SYS01 | [5 empty] | 3 | 55.0459 | BC7 Alcatel 7210 | 2 | A02 BT Utility | 1 | [35 empty] | 0
PTHTL1;DC SYS01 | [5 empty] | 4 | 73.3945 | 6500-14 D04 | 4 | [37 empty] | 0
PTMDN1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
PTMN03;DC SYS01 |  | RA |  |  |  | 2.7 | 49.5413 | UV02 RA | 1.7 | UV03 Alcatel 7210 | 1 | [35 empty] | 0
RATE02;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
RATE02;DC SYS02 | [5 empty] | 0 | 0 | [39 empty] | 0
RCR;DC SYS01 |  | RA |  |  |  | 2.7 | 49.5413 | LM04 RA | 1.7 | LM05 Alcatel 7210 | 1 | [35 empty] | 0
RDGCD2;DC SYS01 |  |  |  | AM |  | 12 | 220.1835 | AA 1-6,AB+AC4-6 Amitie | 12 | [37 empty] | 0
RDG;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
RFDN11;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SBHN01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SDN;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SDNN06;DC SYS02 | [5 empty] | 36.5 | 669.7248 | Q2-7,C11-16 Amitie | 12 | HomeBB DNS YZ15 | 3 | Nokia ILA M12 | 0.5 | CD02 ESA400 | 4 | CD05 Alcatel 7210 | 2 | UV4 MSP7750 PE | 6 | V6 Ciena 5410 | 3 | V7 Ciena 6500 | 3 | V8 iena 6500 | 3 | [21 empty] | 0
SDNN06;DC SYS03 | P-Core | RA | PX |  | OPEX | 10.5 | 192.6606 | Z11 RA | 2.4 | Z12 PX | 0.7 | WX10 Op-EX | 2.1 | WX12 Op-EX | 0.7 | WX9 Op-EX | 1.3 | UV1 Waveserver | 3.3 | [27 empty] | 0
SDNN11;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SDNN13;DC SYS01 | [5 empty] | 10.2 | 187.156 | Google | 1.8 | Netflix | 2.9 | Broadband Capacity | 0.5 | D8 Facebook server | 5 | [31 empty] | 0
SHD;DC SYS01 | [5 empty] | 0.25 | 4.5872 | T02 Alcatel 7210 | 0.25 | [37 empty] | 0
SHDTR1;DC SYS01 |  | RA |  |  |  | 7.2 | 132.1101 | MN06 RA | 1.7 | M5a IGW, M5 IGW | 5.5 | [35 empty] | 0
SHTN03;DC SYS02 |  | RA |  |  |  | 3.7 | 67.8899 | AN/AP02 RA | 1.7 | AB03 BT EAD | 1 | AN/AP03 Alcatel 7210 | 1 | [33 empty] | 0
SLO;DC SYS01 | [5 empty] | 3.5 | 64.2202 | N5 Nokia 1830 ILA | 0.5 | AB04 Alcatel 7210 | 2 | AB03 BT EAD | 1 | [33 empty] | 0
SMHN02;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SNDTM1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
SOL;DC SYS01 | [5 empty] | 2 | 36.6972 | FG03 Bt Util | 1 | FG05 Alcatel 7210 | 1 | [35 empty] | 0
SOSTN1;DC SYS01 | [5 empty] | 2 | 36.6972 | HJ08 Alcatel 7210 | 1 | KL07 BT EAD | 1 | [35 empty] | 0
SOT;DC SYS01 | [5 empty] | 1 | 18.3486 | NP07 Alcatel 7210 SAS-SX | 1 | [37 empty] | 0
SQYN01;DC SYS01 | [5 empty] | 4 | 73.3945 | Alcatel 7210 BE7 | 2 | Alcatel 7210 BE9 | 2 | [35 empty] | 0
SQYN01;DC SYS02 | [5 empty] | 0 | 0 | [39 empty] | 0
SQYN01;DC SYS03 | [5 empty] | 0 | 0 | [39 empty] | 0
SQYN02;DC SYS08a | P-Core |  |  |  |  | 17.05 | 312.844 | GB02 RA | 1.5 | GB03 PX | 0.4 | GB05 Op-ex | 1.5 | GB10 ESA | 1 | GB07 Op-ex | 1.2 | GB09 Op-Ex | 1 | GC02 IGW+WSaI | 0.5 | GC03 QWILT | 2 | GB12 7750SR7 | 3.25 | GC05 Waveserver 5 | 1.6 | JA6 Netflix | 2 | JLJM01 EXFO BV-110 | 1.1 | [15 empty] | 0
SQYN02;DC SYS08b | P-Core | RA | PX |  | OPEX | 16.55 | 303.6697 | GB02 RA | 1 | GB03 PX | 0.6 | GB05 Op-ex | 1.5 | GB10 ESA | 1 | GB07 Op-ex | 1.2 | GB09 Op-Ex | 0.9 | GC02 IGW+WSaI | 0.4 | GC03 QWILT | 2 | GB12 7750SR7 | 3.25 | GC05 Waveserver 5 | 1.6 | JA6 Netflix | 2 | JLJM01 EXFO BV-110 | 1.1 | [15 empty] | 0
SQYN02;DC SYS09a | P-Core |  |  |  |  | 5.75 | 105.5046 | JN04 Juniper SRX 4200 | 0.5 | JQ4 Nokia 7750 SR-7B | 1.25 | JQ5 Nokia 7750 SR-7B | 1.25 | JS3 Nokia 7750 SR-2s | 2.75 | [31 empty] | 0
SQYN02;DC SYS09b | P-Core |  |  |  |  | 5.75 | 105.5046 | JN04 Juniper SRX 4200 | 0.5 | JQ4 Nokia 7750 SR-7B | 1.25 | JQ5 Nokia 7750 SR-7B | 1.25 | JS3 Nokia 7750 SR-2s | 2.75 | [31 empty] | 0
STEDN1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
STGCD1;DC SYS01 | [5 empty] | 3 | 55.0459 | 6500-14 G03 | 3 | [37 empty] | 0
SWNN03;DC SYS01 |  | RA |  |  |  | 3.4 | 62.3853 | JH01 RA | 2.4 | D5 BT EAD | 1 | [35 empty] | 0
SWY;DC SYS01 | [5 empty] | 3 | 55.0459 | EF07 BT EAD | 1 | Alcatel 7210 D3 | 2 | [35 empty] | 0
TELHS1;DC SYS A;EXT ROOM | [5 empty] | 1.1 | 20.1835 | 12/13 G Juniper | 1.1 | [37 empty] | 0
TELHS1;DC SYS B;EXT ROOM | [5 empty] | 0 | 0 | [39 empty] | 0
TELHS1;SYS;A;DC PER02;9D | [5 empty] | 0 | 0 | [39 empty] | 0
TELHS1;SYS;B;DC PER03;1L | [5 empty] | 0 | 0 | [39 empty] | 0
TELHS2;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
TGY;DC SYSA | P-Core |  | PX |  | OPEX | 8.205 | 150.5505 | BC01 PX | 0.9 | BC02 Op-Ex | 1.855 | BC03 Op-Ex | 1.45 | BC04 Op-Ex | 1.9 | Waveserver 5 AB4 | 2.1 | [29 empty] | 0
TGY;DC SYSB **DO NOT CONNECT LOADS** | [5 empty] | 8.205 | 150.5505 | BC01 PX | 0.9 | BC02 Op-Ex | 1.855 | BC03 Op-Ex | 1.45 | BC04 Op-Ex | 1.9 | Waveserver 5 AB4 | 2.1 | [29 empty] | 0
THOTC1;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
TNTTN1-DCSYS01a | [5 empty] | 7.4 | 135.7798 | K&L 1-6 Amitie | 5.8 | E11 Utility Cab | 1.6 | [35 empty] | 0
TNTTN1-DCSYS01b | [5 empty] | 7.7 | 141.2844 | K&L 1-6 Amitie | 5.9 | E11 Utility Cab | 1.8 | [35 empty] | 0
TRON01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
VHXN02;DC SYS01 |  | RA |  |  |  | 7.4 | 135.7798 | DA/DB05 RA | 2.4 | CD10 ISR 4331 | 2 | DA/DB04 Alcatel 7210 | 2 | CD04 BT EAD | 1 | [31 empty] | 0
WADN01;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
WAHP; DC SYS A (Feeds WAHP06) | P-Core | RA | PX |  | OPEX | 10.025 | 183.945 | 3Q RA | 0.9 | 3Z BNG | 1.25 | 1S WS&RLS | 1.55 | 3J WS&RLS | 0.85 | PX 5/6Q | 0.3 | IGW 5/6K | 0.675 | HomeBB DNS 5/6H | 1.5 | 1T WS&RLS | 1.05 | 1V WS&RLS | 0.95 | 5/6E Netflix | 1 | [19 empty] | 0
WAHP; DC SYS B (Feeds WAHP06) | [5 empty] | 11.025 | 202.2936 | 3Q RA | 1.6 | 3Z BNG | 1.25 | 1S WS&RLS | 1.65 | 3J WS&RLS | 0.85 | PX 5/6Q | 0.5 | IGW 5/6K | 0.675 | HomeBB DNS 5/6H | 1.5 | 1T WS&RLS | 1.05 | 1V WS&RLS | 0.95 | 5/6E Netflix | 1 | [19 empty] | 0
WAHP;DC SYS A Tx | [5 empty] | 11.83 | 217.0642 | 20B FACEBOOK | 2 | 20C FACEBOOK | 2 | 20/21E QWILT | 2.73 | 20/21F NOKIA7750 SR-7S | 3 | WS5 20/21G | 2.1 | [29 empty] | 0
WAHP;DC SYS B Tx | [5 empty] | 11.83 | 217.0642 | 20B FACEBOOK | 2 | 20C FACEBOOK | 2 | 20/21E QWILT | 2.73 | 20/21F NOKIA7750 SR-7S | 3 | WS5 20/21G | 2.1 | [29 empty] | 0
WAIP;DC SYS01;GND | [5 empty] | 0 | 0 | [39 empty] | 0
WCKTR1;DCSYS01 | [5 empty] | 1.5 | 27.5229 | C05 Ciena 6500-14 slot | 1.5 | [37 empty] | 0
WHD;DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
WHHN03;DC SYS01 | [5 empty] | 1 | 18.3486 | NP11 Alcatel 7210 | 1 | [37 empty] | 0
WKGN01;DC SYS01 |  | RA |  |  |  | 2.4 | 44.0367 | EF19 RA | 2.4 | [37 empty] | 0
WONTL1; DC SYS02 | [5 empty] | 0.9 | 16.5138 | P03 BT EAD | 0.5 | D06 Ciena 6500 | 0.4 | [35 empty] | 0
WTNTK1;DC SYS01 |  | RA |  |  |  | 2.7 | 49.5413 | L01 RA | 1.7 | L02 Alcatel 7210 | 1 | [35 empty] | 0
WTT;DC SYS01 | [5 empty] | 1 | 18.3486 | SR02 Alcatel 7210 | 1 | [37 empty] | 0
WVHTF1;DCSys01 |  | RA |  |  |  | 2.4 | 44.0367 | AB06 RA | 2.4 | [37 empty] | 0
YRK;DC SYS01 | [5 empty] | 1 | 18.3486 | LM01 Alcatel 7210 | 1 | [37 empty] | 0
YRKTH1; DC SYS01 | [5 empty] | 0 | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
[7 empty] | 0 | [39 empty] | 0
0
Note on K9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211216_4_w122836 - CPL - 3 x Ciena 6500-14 (@2kW each) - in existing racks - Positions G1, H1 & E1
Note on M9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211216_4_w122836 - CPL - 3 x Ciena 6500-14 (@2kW each) - in existing racks - Positions G1, H1 & E1
Note on O9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211216_4_w122836 - CPL - 3 x Ciena 6500-14 (@2kW each) - in existing racks - Positions G1, H1 & E1
Note on J10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced allocation from 4kW to 2kW as only 1 shelf installed. Assumed live load of 1kW. Remaining allocation of 1kW
Note on J12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.2KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.1KW Reply: 2.5kW allocation reduced due to live reading of 1.2KW
Note on L12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8.5kW allocation reduced due to live reading of 3kW Reply: 8.5kW allocation reduced due to live reading of 4.05kW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.5KW Reply: 4.25kW allocation reduced due to live reading of 1.4KW Reply: 4.25kW allocation reduced due to live reading of 1.3KW
Note on N12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.3KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW
Note on P12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of .27KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW
Note on J13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 1.1KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 2KW
Note on L13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 2KW
Note on N13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW
Note on J14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ciena 6500-7slot[400Watts]new rack has been planned- CPL Removal project ORMT_SAP_240123_21_Y850155
Note on J18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on L22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 116A, so original 8kW reduced down Reply: 4kW allocation reduced due to live reading of 3.6KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7KW
Note on N22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 44.5A so original 4kW reduced down Reply: 4kW allocation reduced due to live reading of 1.1KW Reply: Allocation for RA should be 2.5kW per side so remaining allocated value updated Reply: 2.5KW allocation reduced to live reading of 1.2KW Reply: 2.5KW allocation reduced to live reading of 1KW Reply: 2.5KW allocation reduced to live reading of 1KW Reply: 2.5KW allocation reduced to live reading of 1KW Reply: 2.5KW allocation reduced to live reading of 1.1KW Reply: 2.5KW allocation reduced to live reading of 0.8KW Reply: 2.5KW allocation reduced to live reading of 1.4KW Reply: 2.5KW allocation reduced to live reading of 1.2KW Reply: 2.5KW allocation reduced to live reading of 1.3KW
Note on P22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 12.2A so original 4.5kW reduced down Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.7KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.7KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW
Note on R22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 35.4A so original 4.5kW reduced by 1.9kW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW
Note on T22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 17.2A so original 4.5kW reduced by 950w Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.4KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW
Note on X22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.3KW
Note on Z22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ESA400s @ 520W each only 2 planned day 1 Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.3KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5KW
Note on L23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 116A, so original 8kW reduced down Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.6KW Reply: 4kW allocation reduced due to live reading of 3.6KW Reply: 4kW allocation reduced due to live reading of 3.6KW
Note on N23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 44.5A so original 4kW reduced down Reply: 4kW allocation reduced due to live reading of 2KW Reply: Allocation for RA should be 2.5kW per side so remaining allocated value updated Reply: 2.5KW allocation reduced due to live reading of 1.8KW Reply: 2.5KW allocation reduced due to live reading of 2KW Reply: 2.5KW allocation reduced due to live reading of 2.1KW Reply: 2.5KW allocation reduced due to live reading of 2.1KW Reply: 2.5KW allocation reduced due to live reading of 1.9KW Reply: 2.5KW allocation reduced due to live reading of 2.3KW Reply: 2.5KW allocation reduced to live reading of 2KW Reply: 2.5KW allocation reduced to live reading of 2.2KW Reply: 2.5KW allocation reduced to live reading of 2.1KW
Note on P23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 12.2A so original 4.5kW reduced down Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.7KW Reply: 2.25kW allocation reduced due to live reading of 0.7KW Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW
Note on R23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 35.4A so original 4.5kW reduced by 1.9kW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.3KW Reply: 2.25kW allocation reduced due to live reading of 1.3KW Reply: 2.25kW allocation reduced due to live reading of 1.3KW Reply: 2.25kW allocation reduced due to live reading of 1.3KW
Note on T23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 17.2A so original 4.5kW reduced by 950w Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW Reply: 2.25kW allocation reduced due to live reading of 0.5KW
Note on X23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 0.1KW Reply: 2.5kW allocation reduced due to live reading of 0.1KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW Reply: 2.5kW allocation reduced due to live reading of 0.2KW
Note on Z23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ESA400s @ 520W each only 2 planned day 1 Reply: 2kW allocation reduced due to live reading of 0.3KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.3KW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.6KW Reply: 2kW allocation reduced due to live reading of 0.6KW
Note on J25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on M25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ciena 6500 14slot and Alcatel 7210 SAS SX Planned - ORMT_SAP_231025_22_Y858601
Note on O25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on Q25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on J26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on L26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3kW original allocation reduced by 1kW (estimated) to 2kW for shelf 1. Second shelf planned
Note on N26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3kW allocation for 2 x 6500-14 shelves. Confirmed installed. Estimated reading of 2kW. Allocation remaining 1kW
Note on Q26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on S26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on U26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IGW(3.5KW) into L06-ORMT_SAP_231011_4_10335416
Note on J30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 6.3kW, so original 8kW reduced Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW
Note on L30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5kW allocation reduced due to live reading of 1KW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 0.6kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.5kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW
Note on N30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on P30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 17.4A so original 4.5kW reduced by 950w Reply: 2.25kW allocation reduced due to live reading of 0.7KW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW
Note on R30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 34.4A so original 4kW reduced by 1.9kW Reply: 2kW allocation reduced due to live reading of 1KW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.2kW
Note on T30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7W
Note on V30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: John Womersley. provisional allocation for end of life load Reply: 2.1kW allocation reduced due to live reading of 0.1kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW
Note on J31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 6.3kW, so original 8kW reduced Reply: 4kW allocation reduced due to live reading of 3.4KW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW
Note on L31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.7kW Reply: 2.5kW allocation reduced due to live reading of 2.2kW Reply: 2.5kW allocation reduced due to live reading of 2.2kW Reply: 2.5kW allocation reduced due to live reading of 2.1kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW
Note on N31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of .07 KW so original 1kW
Note on P31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 17.4A so original 4.5kW reduced by 950w Reply: 2.25kW allocation reduced due to live reading of 0.6KW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW
Note on R31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 34.4A so original 4kW reduced by 1.9kW Reply: 2kW allocation reduced due to live reading of 1.1KW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 1.2kW
Note on T31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.67W
Note on V31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: John Womersley. provisional allocation for end of life load Reply: 2.1kW allocation reduced due to live reading of 0.1kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW
Note on J32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incase of fault scenario - 19kW max draw from single system
Note on Q37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New AKAMAI rack is planned with a removal of an existing 2 racks in BL12 & BL13 under ORMT_SAP_231220_15_10335416 with power 5KW
Note on S37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New AKAMAI rack is planned in BE09 under ORMT_SAP_231220_15_10335416
Note on J38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incase of fault scenario - 19kW max draw from single system
Note on K38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDU installation planned for ORMT_SAP_240424_8_11407175
Note on J39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 74A, so 38kW allocation reduced by 4kW Reply: 19kW allocation reduced due to live reading of 0.8kW Reply: 19kW allocation reduced due to live reading of 0.2kW Reply: 19kW allocation reduced due to live reading of 0.1kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 3.9kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 3.8kW
Note on L39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 249A, so allocation of 67kW reduced to 53.43kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 13.4kW Reply: 67kW allocation reduced due to live reading of 13.5kW
Note on N39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kW, live reading of 2.5kW so reduced Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW
Note on P39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8kW, live reading of 6kW so reduced. Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.2kW
Note on R39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 50A, so 4kW allocation reduced by 2.7kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3.3kW
Note on T39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 43.5A, so 4kW allocation reduced by 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW
Note on V39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 20A, so 4kW allocation reduced by 1.1kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 3.1kW Reply: 4kW allocation reduced due to live reading of 3.1kW
Note on X39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on Z39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on AB39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 60A, so 6kW allocation reduced by 3.2kW Reply: 6kW allocation reduced due to live reading of 3.4kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.6kW
Note on AD39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 101A, so 6.5kW allocation reduced by 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW
Note on AF39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 2.1kW
Note on AN39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 14.2kW allocation reduced due to live reading of 2kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW
Note on AP39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_220607_5_10335416 3.13kW required
Note on AR39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_231109_20_10335416
Note on J40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 74A, so 38kW allocation reduced by 4kW Reply: 19kW allocation reduced due to live reading of 0.8kW Reply: 19kW allocation reduced due to live reading of 0.2kW Reply: 19kW allocation reduced due to live reading of 0.1kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 3.9kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 3.8kW
Note on L40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 249A, so allocation of 67kW reduced to 53.43kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 13.4kW Reply: 67kW allocation reduced due to live reading of 13.5kW
Note on N40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kW, live reading of 2.5kW so reduced Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW
Note on P40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8kW, live reading of 6kW so reduced. Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.2kW
Note on R40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 50A, so 4kW allocation reduced by 2.7kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW
Note on T40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 43.5A, so 4kW allocation reduced by 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW
Note on V40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 20A, so 4kW allocation reduced by 1.1kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 3.1kW Reply: 4kW allocation reduced due to live reading of 3.1kW
Note on X40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on Z40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on AB40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 60A, so 6kW allocation reduced by 3.2kW Reply: 6kW allocation reduced due to live reading of 3.4kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.6kW
Note on AD40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 101A, so 6.5kW allocation reduced by 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW
Note on AF40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 2.1kW
Note on AN40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 14.2kW allocation reduced due to live reading of 2kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW
Note on AP40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_220607_5_10335416 3.13kW required
Note on AR40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_231109_20_10335416
Note on K44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DE4 utility rack is planned under ORMT_SAP_230907_9_Y850155
Note on J46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ciena 6500-7slot[400Watts] new rack has been planned- CPL Removal project ORMT_SAP_240123_21_Y850155
Note on G48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: BSHn08 iPDUs across Sys 1 and 2 so loads split
Note on J48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kw, live reading of 2.5kW so reduced down Reply: 2.5kW allocation reduced due to live reading of 1.2KW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW
Note on L48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8Kw, live reading of 6kW, so reduced down Reply: 4kW allocation reduced due to live reading of 3.7KW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.8kW Reply: 4kW allocation reduced due to live reading of 3.8kW
Note on N48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on P48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on R48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.7KW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW
Note on T48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.3KW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on V48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.3KW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW
Note on X48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kw allocation reduced due to live reading of 4kW Reply: 3kW allocation reduced due to live reading of 1.8KW Reply: 3kW allocation reduced due to live reading of 1.8kW Reply: 3kW allocation reduced due to live reading of 1.8kW Reply: 3kW allocation reduced due to live reading of 2kW Reply: 3kW allocation reduced due to live reading of 1.9kW Reply: 3kW allocation reduced due to live reading of 1.9kW Reply: 3kW allocation reduced due to live reading of 2kW Reply: 3kW allocation reduced due to live reading of 2kW
Note on Z48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.9KW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW
Note on AD48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 0.3kW
Note on AF48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2x N9K – 674W 1x ISR4331 – 42W 4x QB500 – 2414W
Note on AH48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW Reply: 4kW allocation reduced due to live reading of 2.9kW
Note on AL48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.1KW Reply: 0.5kW allocation reduced due to live reading of 0.1KW
Note on J49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kw, live reading of 2.5kW so reduced down Reply: 2.5kW allocation reduced due to live reading of 1.6KW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.7kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW
Note on L49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 2Kw, live reading of 6kW, so reduced down Reply: 4kW allocation reduced due to live reading of 3.5KW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.5kW
Note on N49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on P49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW
Note on R49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.7KW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW
Note on T49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on V49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.3KW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.3kW
Note on X49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kw allocation reduced due to live reading of 4kW Reply: 3kW allocation reduced due to live reading of 2.1KW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW
Note on Z49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.9KW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW
Note on AD49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW
Note on AF49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2x N9K – 674W 1x ISR4331 – 42W 4x QB500 – 2414W
Note on AH49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW
Note on AL49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of .06 KW so original 1kW Reply: 0.5kW allocation reduced due to live reading of 0.1KW Reply: 0.5kW allocation reduced due to live reading of 0.1KW Reply: 0.5kW allocation reduced due to live reading of 0.1KW Reply: 0.5kW allocation reduced due to live reading of 0.1KW
Note on AN49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: BSHN04 G08. Load transfer from ground floor systems to take place later this year 2023. Loads currently fed from ground floor.
Note on J50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 40A, so 3kW allocation reduced by 2.2kW
Note on L50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 36A, so 3kW allocation reduced by 2kW
Note on N51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8.7kW Load transfer from ground floor systems to take place later this year 2023. Loads currently fed from ground floor.
Note on P51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: BSHN04 G08. Load transfer from ground floor systems to take place later this year 2023. Loads currently fed from ground floor.
Note on R51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for virgin media NTE rack BH18- ORMT_SAP_240102_12_Y855684
Note on S51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C02- ORMT_SAP_240425_5_10330814x
Note on U51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C04- ORMT_SAP_240425_5_10330814x
Note on N52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8.7kW Load transfer from ground floor systems to take place later this year 2023. Loads currently fed from ground floor.
Note on P52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: BSHN04 G08. Load transfer from ground floor systems to take place later this year 2023. Loads currently fed from ground floor.
Note on R52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for virgin media NTE rack BH18- ORMT_SAP_240102_12_Y855684
Note on S52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C02- ORMT_SAP_240425_5_10330814x
Note on U52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C04- ORMT_SAP_240425_5_10330814x
Note on J54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 5kW to 3kW based on figures for other RA's Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW
Note on L54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8kw, live readings show running at 6.7kW currently Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW
Note on N54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.2KW
Note on P54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2.5kW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 3KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 3.4KW Reply: 4kW allocation reduced due to live reading of 3.2KW Reply: 4kW allocation reduced due to live reading of 3KW Reply: 4kW allocation reduced due to live reading of 2.7KW
Note on R54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 16kW allocations reduced due to live reading of 4kW Reply: Live reading of 5kW allocated load remaining 11kW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 6kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5.3KW Reply: 16kW allocation reduced due to live reading of 5.5KW Reply: 16kW allocation reduced due to live reading of 5.1KW
Note on V54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 7kW allocation reduced due to live reading of 1.5kW Reply: Updated live reading of 5.3kW remaining allocation 1.7kW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 4.8KW Reply: 7kW allocation reduced due to live reading of 4.8KW Reply: 7kW allocation reduced due to live reading of 5.2KW
Note on X54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3.7kW allocation reduced due to live reading of 1.5kW Reply: 3.7kW allocation reduced due to Live reading of 1.7kW Reply: 1kW added, taken from QWILT as now 10x server 4.25kW requirement Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW
Note on AD54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1x UCS C220 – 603W Reply: updated to 880W Reply: Reduced from 4kW to give to additional 1kW FB Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW
Note on AF54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Google rack new allocated load of 4.5kW. Live load 2kW remaining allocation 2.5kW Reply: 4.5kW allocation reduced due to live reading of 2.3KW
Note on AJ54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ESA400s @ 520W each only 2 planned day 1 Reply: 4kW allocation reduced due to live reading of 0.2KW Reply: 4kW allocation reduced due to live reading of 0.9KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 1.1KW
Note on J57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 3.2KW Reply: 5kW allocation reduced due to live reading of 3.2KW
Note on L57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed running at 6kW at the moment Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.9KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW
Note on N57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated actual load readings from AxScada; 3.4kW used; 10.3kW remaining Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5.1KW Reply: 14kW allocation reduced due to live reading of 5.1KW Reply: 14kW allocation reduced by 1kW per rack, 3kW total. New Allocation 11kW . 5.1kW live reading remaining allocation of 5.9kW Reply: 11kW allocation reduced due to live reading of 5.2KW Reply: 11kW allocation reduced due to live reading of 5.4KW Reply: 11kW allocation reduced due to live reading of 5.6KW Reply: 11kW allocation reduced due to live reading of 6.2KW Reply: 11kW allocation reduced due to live reading of 6.3KW
Note on P57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4kW due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.4KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.5KW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.7KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.1KW
Note on R57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4kW due to live reading of 2.3kW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW
Note on T57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW
Note on V57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 7kW after live readings of 3.5kW Reply: 7kW allocation reduced due to live reading of 4KW Reply: 7kW allocation reduced due to live reading of 4.1KW Reply: 7kW allocation reduced due to live reading of 4.1KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.5KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 5.1KW
Note on X57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 3.7kW due to live reading of 1.1kW Reply: 3.7kW allocation reduced due to live reading of 1.3KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.6KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.5KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.5KW Reply: 3.7kW allocation reduced due to live reading of 1.6KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW
Note on Z57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 2.6kW due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.2KW Reply: 2.6kW allocation reduced due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.4kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.3kW Reply: 2.6kW allocation reduced due to live reading of 1.3kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.4kW
Note on AB57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NCS-57C3 - 500W - 2 feeds
Note on AD57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 10.9kW allocation reduced due to live reading of 0.5kW Reply: Allocation correct to 6.5kW, but showing reduced to 6kW due to live reading of 0.5kW Reply: 6.5kW allocation reduced due to live reading of 0.5kW
Note on AF57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW
Note on AH57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ESA400s @ 520W each only 2 planned day 1 Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on AJ57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW
Note on AK57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Waveserver_5(2.0KW)into B22-ORMT_SAP_231123_10_w014433
Note on AM57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 10 Servers and 1 Switch planned - ORMT_SAP_240306_5_10335416
Note on J58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on U70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Ciena 6500-7(1.1KW) into existing cab AB2-ORMT_SAP_231122_3_26168659
Note on W70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 40 Amps for NOKIA 7250 AND ORACLE ACME 6350 is planned under ORMT_SAP_240426_16_10330814x
Note on Y70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 40 Amps for NOKIA 7250 AND ORACLE ACME 6350 is planned under ORMT_SAP_240426_16_10330814x
Note on L72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.7KW Reply: 2.5kW allocation reduced due to live reading of 1.6KW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.5KW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.6KW Reply: 2.5kW allocation reduced due to live reading of 1.6KW Reply: 2.5kW allocation reduced due to live reading of 2.1KW
Note on N72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW
Note on P72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 2.25kW allocation reduced due to live reading of 1.4KW Reply: 2.25kW allocation reduced due to live reading of 1.5KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.8KW Reply: 2.25kW allocation reduced due to live reading of 1.8KW
Note on R72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW
Note on T72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 102A, so 6.5kW allocation reduced by 5.5kW Reply: 3.25kW allocation reduced due to live reading of 3KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 3KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW Reply: 3.25kW allocation reduced due to live reading of 2.9KW
Note on L73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5kW allocation reduced due to live reading of 1.7KW Reply: 2.5kW allocation reduced due to live reading of 1.2KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.5KW Reply: 2.5kW allocation reduced due to live reading of 1.6KW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.5KW Reply: 2.5kW allocation reduced due to live reading of 1.3KW Reply: 2.5kW allocation reduced due to live reading of 1.4KW Reply: 2.5kW allocation reduced due to live reading of 1.6KW
Note on N73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.8KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW
Note on P73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 2.25kW allocation reduced due to live reading of 1.4KW Reply: 2.25kW allocation reduced due to live reading of 1.4KW Reply: 2.25kW allocation reduced due to live reading of 1.5KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.5KW Reply: 2.25kW allocation reduced due to live reading of 1.5KW Reply: 2.25kW allocation reduced due to live reading of 1.6KW Reply: 2.25kW allocation reduced due to live reading of 1.8KW Reply: 2.25kW allocation reduced due to live reading of 1.8KW
Note on R73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 0.9KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW Reply: 2.25kW allocation reduced due to live reading of 1.1KW
Note on T73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 102A, so 6.5kW allocation reduced by 5.5kW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.7KW Reply: 3.25kW allocation reduced due to live reading of 2.6KW Reply: 3.25kW allocation reduced due to live reading of 2.7KW Reply: 3.25kW allocation reduced due to live reading of 2.7KW Reply: 3.25kW allocation reduced due to live reading of 2.7KW
Note on J74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW
Note on J75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW
Note on S76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade given for ORMT_SAP_240415_18_Y854576
Note on S77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade given for ORMT_SAP_240415_18_Y854576
Note on J80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW
Note on J81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW
Note on J83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kw to 3kW estimated usage
Note on I86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This rack is planned for Alcatel 1626 & Ciena 6500- 7 slot installation under ORMT_SAP_240110_7_26168659[DCTN03 site closure]
Note on J91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 5kW Reply: Original 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on Q94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Marconi MSPP 1684 is planned under ORMT_SAP_231103_12_y842157
Note on J102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 9th Aug - reduced to 1.5kW as now on (using figures for other nodes) Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW
Note on L102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 9th Aug reduced to 2.5kw as turn on (using figures from other live sites) originally 8kW Reply: 4kW allocation reduced due to live reading of 3.3kW Reply: 4kW allocation reduced due to live reading of 3.3kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW
Note on N102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW
Note on P102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on R102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW
Note on T102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on V102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW
Note on AF102: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.3kW allocation reduced due to live reading of 0.6kW Reply: 1.3kW allocation reduced due to live reading of 0.6kW
Note on J103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load split across both power systems Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW
Note on L103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load split across both power systems Reply: 4kW allocation reduced due to live reading of 3.3kW Reply: 4kW allocation reduced due to live reading of 3.3kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW
Note on N103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.3kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW
Note on P103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on R103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW
Note on T103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on V103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on AF103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.3kW allocation reduced due to live reading of 0.1kW Reply: 1.3kW allocation reduced due to live reading of 0.1kW
Note on G104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 11.2 kW split across A&B systems
Note on T104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1x UCS C220 – 603W
Note on V104: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NCS-57C3 - 500W - 2 feeds
Note on J109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW
Note on J110: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW
Note on J114: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW
Note on J115: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW
Note on J116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on M116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional ADVA XG120 into existing cab H7 planned under ORMT_SAP_240202_13_w019357
Note on J117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 7.7Amps/420W. Allocation reduced by 0.5kW from 5.5 to 5 Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW
Note on L117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 7Amps/380W. Allocation reduced by 0.4kW from 5.5 to 5.1 Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW
Note on N117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 49Amps/2.7kW. Allocation reduced by 2.7kW from 5 to 2.3kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1kW
Note on P117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on R117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW
Note on J118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 7.7Amps/420W. Allocation reduced by 0.5kW from 5.5 to 5 Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW
Note on L118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 7Amps/380W. Allocation reduced by 0.4kW from 5.5 to 5.1 Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW
Note on N118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1/2/22 - Clamp meter reading shows running load of 49Amps/2.7kW. Allocation reduced by 2.7kW from 5 to 2.3kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW
Note on P118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on R118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.1kW Reply: 0.5kW allocation reduced due to live reading of 0.2kW
Note on J119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW total allocation reduced due to live reading of 6.5kW
Note on L119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW
Note on N119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on P119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.8kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 2.1kW Reply: 2.5kW allocation reduced due to live reading of 2.1kW Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 2.2kW Reply: 2.5kW allocation reduced due to live reading of 2.2kW Reply: 2.5kW allocation reduced due to live reading of 2.2kW
Note on R119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW total allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on T119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW total allocation reduced due to live reading of 0.5kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on V119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x2 6500-14 shelves, agreed to reduce allocation at NIR 23/11/23 to 1.5kW per shelf from 2kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on X119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.3kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW
Note on Y119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver rack is planned under CPL removal project. Reply: Allocation limited to 1.5kW, x1 RLS R4 (450W) and x1 Waveserver AI (900W) Reply: 2.5kW allocation reduced due to live reading of 0.5kW
Note on AA119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: WAVESERVER 5 Rack is planned- ORMT_SAP_231110_8_w014433 Reply: Allocation limited to 2kW, x1 Waveserver5 Reply: 2.5kW allocation reduced due to live reading of 0.2kW
Note on J120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW total allocation reduced due to live reading of 6.5kW
Note on L120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.7kW
Note on N120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on P120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.8kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 0.6kW Reply: 2.5kW allocation reduced due to live reading of 0.7kW Reply: 2.5kW allocation reduced due to live reading of 0.7kW
Note on R120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW total allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on T120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW total allocation reduced due to live reading of 0.5kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.3kW
Note on V120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x2 6500-14 shelves, agreed to reduce allocation at NIR 23/11/23 to 1.5kW per shelf from 2kW Reply: 2kW allocation reduced due to live reading of 0.1kW
Note on X120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.3kW
Note on Y120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver rack is planned under CPL removal project. Reply: Allocation limited to 1.5kW, x1 RLS R4 (450W) and x1 Waveserver AI (900W) Reply: 2.5kW allocation reduced due to live reading of 0.4kW
Note on AA120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: WAVESERVER 5 Rack is planned- ORMT_SAP_231110_8_w014433 Reply: Allocation limited to 2kW, x1 Waveserver5 Reply: 2.5kW allocation reduced due to live reading of 0.2kW
Note on J121: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on I123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: awaiting floorplan update
Note on K123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A06 - Power upgrade for 40 amps ( 2.2Kw )under ORMT_SAP_240326_7_Y854539
Note on J129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kW to 3kW estimated usage Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on O129: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional BT EAD[KA7] 0.5 kw into existing cab C03-ORMT_SAP_231218_9_Y861526
Note on J131: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kw to 3kW estimated usage Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated 2kW reduction as box now in service. Reduced from 5kW to 3kW Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 5 to 3kW estimated (confirmed by Rich) Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on L134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4.5 to 2kW estimated (confirmed by Rich)
Note on J136: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kW to 3kW estimated Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J139: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional power has been added under ORMT_SAP_240508_11_Y854105
Note on J140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.4kW Reply: 5kW allocation reduced due to live reading of 3.5kW Reply: 5kW allocation reduced due to live reading of 3.5kW Reply: 5kW allocation reduced due to live reading of 3.9kW Reply: 5kW allocation reduced due to live reading of 3.9kW
Note on L140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 1kW Reply: 5kW allocation reduced due to live reading of 0.1kW
Note on N143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 67A, so 16kW allocation reduced by 3.7kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 3.1kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.2kW Reply: 4kW allocation reduced due to live reading of 3.3kW
Note on S143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211015_16_11135118
Note on V143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: John Womersley. Provisional allocation for end of life Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.2kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW
Note on Z143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.3kW
Note on AB143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1x UCS C220 – 603W Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW
Note on AD143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NCS-57C3 - 500W - 2 feeds
Note on AJ143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade planned under ORMT_SAP_231017_2_Y855640
Note on AL143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for 10 servers, but 6 servers to be installed from Day1 ORMT_SAP_231011_14_10335416
Note on AN143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for additional 2 servers, to the existing 8,. 10 servers total for the rack ORMT_SAP_231011_14_10335416
Note on J144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 0.5kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.3kW Reply: 2.5kW allocation reduced due to live reading of 0.1kW Reply: 2.5kW allocation reduced due to live reading of 0.4kW
Note on L144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW
Note on N144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.8kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.6kW
Note on V144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.1kW allocation reduced due to live reading of 0.3kW
Note on Z144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.5kW allocation reduced due to live reading of 0.3kW
Note on AB144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW
Note on AJ144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade planned under ORMT_SAP_231017_2_Y855640
Note on AL144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for 10 servers, but 6 servers to be installed from Day1 ORMT_SAP_231011_14_10335416
Note on AN144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for additional 2 servers, to the existing 8,. 10 servers total for the rack ORMT_SAP_231011_14_10335416
Note on J145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Planned for ORMT_SAP_231013_6_w014433
Note on J146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on M146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade given for ORMT_SAP_230607_9_Y854413
Note on J148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J151: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on Q152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 30kW ring fenced for WACS CoLo contract
Note on T152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Ciena 6500-14 slot with power upgrade in existing CAB F03- ORMT_SAP_230821_19_26168659
Note on J155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: provisional allocation for end of life load Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW
Note on L155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.2kW
Note on P155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 22A, so 4kW allocation reduced by 1.2kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW
Note on R155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 30A, so 4kW allocation reduced by 1.6kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW
Note on T155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 14A, so 4kW allocation reduced by 800W Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.8kW
Note on V155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW
Note on X155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on Y155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver rack is planned- CPL removal project.
Note on Z155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.8kW Reply: 5kW allocation reduced due to live reading of 0.8kW
Note on J159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 84A, so 12kW allocation reduced by 4.5kW Reply: 6kW allocation reduced due to live reading of 2.9kW Reply: 6kW allocation reduced due to live reading of 2.9kW Reply: 6kW allocation reduced due to live reading of 2.8kW Reply: 6kW allocation reduced due to live reading of 3kW Reply: 6kW allocation reduced due to live reading of 2.9kW Reply: 6kW allocation reduced due to live reading of 3.2kW Reply: 6kW allocation reduced due to live reading of 3.1kW Reply: 6kW allocation reduced due to live reading of 3.4kW Reply: 6kW allocation reduced due to live reading of 3.4kW
Note on L159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW total but confirmed currently running at 3.5kW, so 0.75kw left per system Reply: 2.5kW allocation reduced due to live reading of 2kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW
Note on R159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6kW allocation reduced due to onsite reading of 3.9kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.4kW Reply: 3kW allocation reduced due to live reading of 2.4kW
Note on T159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW
Note on V159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.45kW allocation reduced due to live reading of 0.5kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW
Note on X159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Totla 4.5kW allocation reduced due to live reading of 2kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.8kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.5kW
Note on Z159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.4kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.4kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.4kW Reply: 0.9kW allocation reduced due to live reading of 0.4kW
Note on AB159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6.5kW reduced due to 5.6kW live reading Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.9kW Reply: 3.25kW allocation reduced due to live reading of 2.9kW Reply: 3.25kW allocation reduced due to live reading of 2.9kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.9kW Reply: 3.25kW allocation reduced due to live reading of 2.9kW
Note on AD159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 2.2kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on AF159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW
Note on AH159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.75kW allocation reduced due to live reading of 0.6kW Reply: 2.75kW allocation reduced due to live reading of 0.6kW
Note on AJ159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW Reply: 2kW allocation reduced due to live reading of 0.9kW
Note on AL159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AN159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AP159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AR159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on AT159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW
Note on J160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 84A, so 12kW allocation reduced by 4.5kW Reply: 6kW allocation reduced due to live reading of 2.6kW Reply: 6kW allocation reduced due to live reading of 2.8kW Reply: 6kW allocation reduced due to live reading of 2.9kW Reply: 6kW allocation reduced due to live reading of 3kW Reply: 6kW allocation reduced due to live reading of 3.1kW Reply: 6kW allocation reduced due to live reading of 3.2kW Reply: 6kW allocation reduced due to live reading of 3.2kW Reply: 6kW allocation reduced due to live reading of 3.5kW Reply: 6kW allocation reduced due to live reading of 3.6kW
Note on L160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW total but confirmed currently running at 3.5kW, so 0.75kw left per system Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.7kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 1.9kW Reply: 2.5kW allocation reduced due to live reading of 1.8kW Reply: 2.5kW allocation reduced due to live reading of 2kW
Note on R160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6kW allocation reduced due to onsite reading of 3.9kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.4kW Reply: 3kW allocation reduced due to live reading of 2.4kW
Note on T160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW
Note on V160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.45kW allocation reduced due to live reading of 0.5kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW Reply: 1.45kW allocation reduced due to live reading of 0.6kW
Note on X160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Totla 4.5kW allocation reduced due to live reading of 2kW Reply: 2.25 kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.6kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW
Note on Z160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW Reply: 0.9kW allocation reduced due to live reading of 0.5kW
Note on AB160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6.5kW reduced due to 5.6kW live reading Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW Reply: 3.25kW allocation reduced due to live reading of 2.8kW
Note on AD160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 2.2kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on AF160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW Reply: 2.1kW allocation reduced due to live reading of 0.3kW
Note on AH160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.75kW allocation reduced due to live reading of 0.7kW Reply: 2.75kW allocation reduced due to live reading of 0.7kW
Note on AJ160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW
Note on AL160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AN160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AP160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AR160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on AT160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW
Note on J162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional XG210 is planned in existing rack E10 under ORMT_SAP_240212_3_w019357
Note on J169: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kW to 3kW estimated usage Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J171: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 2.5kW allocation reduced due to live reading of 2.1kW
Note on L172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 6kW allocation reduced due to live reading of 0.9kW
Note on N172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on Q172: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_230809_13_Y854576 - Given for power upgrade
Note on J173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW
Note on L173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 6kW allocation reduced due to live reading of 0.8kW
Note on N173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on Q173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_230809_13_Y854576 - Given for power upgrade
Note on J178: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5 kW allocation reduced due to live reading of 1.6 kW Reply: 2.5 kW allocation reduced due to live reading of 1.7 kW Reply: 2.5 kW allocation reduced due to live reading of 1.7 kW Reply: 2.5 kW allocation reduced due to live reading of 1.3 kW Reply: 2.5 kW allocation reduced due to live reading of 1.3 kW Reply: 2.5 kW allocation reduced due to live reading of 1.3 kW Reply: 2.5 kW allocation reduced due to live reading of 1.7kW Reply: 2.5 kW allocation reduced due to live reading of 1.5kW
Note on J179: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 2.5 kW allocation reduced due to live reading of 0.8 kW Reply: 2.5 kW allocation reduced due to live reading of 0.8 kW Reply: 2.5 kW allocation reduced due to live reading of 0.8 kW Reply: 2.5 kW allocation reduced due to live reading of 1.1 kW Reply: 2.5 kW allocation reduced due to live reading of 1.7 kW Reply: 2.5 kW allocation reduced due to live reading of 0.8 kW Reply: 2.5 kW allocation reduced due to live reading of 1.1kW Reply: 2.5 kW allocation reduced due to live reading of 1.1kW Reply: 2.5 kW allocation reduced due to live reading of 0.8 kW Reply: 2.5 kW allocation reduced due to live reading of 1kW
Note on L179: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6 kW allocation reduced due to live reading of 0.1 kW Reply: 6 kW allocation reduced due to live reading of 0.1 kW Reply: 6 kW allocation reduced due to live reading of 0.1 kW Reply: 6 kW allocation reduced due to live reading of 0.1 kW Reply: 6 kW allocation reduced due to live reading of 0.1 kW Reply: 6 kW allocation reduced due to live reading of 0.1 kW
Note on J184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 45A, so 5kW allocation reduced by 2.5kW Reply: 1.25kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 0.2kW Reply: 2.5kW allocation reduced due to live reading of 0.5kW Reply: 2.5kW allocation reduced due to live reading of 0.3KW Reply: 2.5kW allocation reduced due to live reading of 0.5KW Reply: 2.5kW allocation reduced due to live reading of 0.4KW
Note on L184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 3.8kW Reply: 6kW allocation reduced due to live reading of 3.9kW Reply: Allocated load corrected back to 6kW as the 3.9kW reading is due to spurious load on AxScada Reply: 6kW allocation reduced due to live reading of 0.1kW
Note on N184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.1kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.1kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on J185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 45A, so 5kW allocation reduced by 2.5kW
Note on J187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 45A, so 5kW allocation reduced by 2.5kW
Note on L187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 6kW allocation reduced due to live reading of 0.3kW
Note on P187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 1.2kW
Note on R187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on J188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 45A, so 5kW allocation reduced by 2.5kW
Note on P188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 1.2kW
Note on R188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW Reply: 1kW allocation reduced due to live reading of 0.1kW
Note on K190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Utility Cab planned for ORMT_SAP_240301_3_Y857169
Note on J194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: The allocation for the RA should be 5kW. Updated with reading of 2.6kW removed from 5kW allocation. 2.4kW remaining. Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW
Note on L204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW
Note on N204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 34.4A, so 4kW allocation reduced by 1.8kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW
Note on P204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 14.4A, so 4kW allocation reduced by 800W Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 01.3kW
Note on R204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 34A, so 4kW allocation reduced by 1.8kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW
Note on T204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.7kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.8kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW
Note on N206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NCS-57C3 - 500W - 2 feeds
Note on O206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 1*100 amps power upgrade is planned for ORMT_SAP_240306_5_10335416
Note on J208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: estimated 2kW reduction from 5kW to 3kW. Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 2.5kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 0.8kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1kW
Note on L219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6.7kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW
Note on N219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4 due to live reading of 700w Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on P219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW
Note on R219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 23A, so 4kW allocation reduced by 1.2kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW
Note on T219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 23A, so 4kW allocation reduced by 1.2kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW
Note on V219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live redaing of 4kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.4kW Reply: 3kW allocation reduced due to live reading of 2.4kW Reply: 3kW allocation reduced due to live reading of 2.4kW Reply: 3kW allocation reduced due to live reading of 2.5kW
Note on X219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW
Note on AB219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on AE219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDU installation planned for ORMT_SAP_240424_8_11407175
Note on J220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 2.5kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW
Note on L220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6.7kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW
Note on N220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4 due to live reading of 700w Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on P220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 1kW Reply: 2kW allocation reduced due to live reading of 1kW
Note on R220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 23A, so 4kW allocation reduced by 1.2kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW
Note on T220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 23A, so 4kW allocation reduced by 1.2kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.7kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 0.8kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW Reply: 2kW allocation reduced due to live reading of 1.1kW
Note on V220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live redaing of 4kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.2kW Reply: 3kW allocation reduced due to live reading of 2.1kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.3kW Reply: 3kW allocation reduced due to live reading of 2.6kW
Note on X220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW Reply: 2.7kW allocation reduced due to live reading of 0.7kW
Note on AB220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on AE220: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDU installation planned for ORMT_SAP_240424_8_11407175
Note on O221: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Nokia 7750 SR-2s,Nokia 7210 SAS-S 110GE is planned in an existing cab JS3 under ORMT_SAP_231012_19_26168659
Note on O222: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Nokia 7750 SR-2s,Nokia 7210 SAS-S 110GE is planned in an existing cab JS3 under ORMT_SAP_231012_19_26168659
Note on J225: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced by 2.5kW as per other live RA readings Reply: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on I227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2*Juniper QFX5110 planned - ORMT_SAP_231020_19_26168659
Note on J232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocation reduced to 1.8kW after live reading of 6.2kW
Note on L232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 3.71kW after 790w live reading
Note on N232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 2.9kW after live reading of 1.6kW
Note on P232: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 3.8kW after live reading of 692w
Note on J233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocation reduced to 1.8kW after live reading of 6.2kW
Note on L233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 3.71kW after 790w live reading
Note on N233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 2.9kW after live reading of 1.6kW
Note on P233: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced to 3.8kW after live reading of 692w
Note on J235: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.2kW
Note on L235: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on J236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.1kW
Note on L236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on J238: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on J240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 3.1kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.3kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.5kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.4kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW Reply: 2.5kW allocation reduced due to live reading of 1.6kW
Note on L240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocated, live so halved to 2.5kw
Note on N240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 79A, so 13.5kW allocation reduced by 4.3kW Reply: 6.75kW allocation reduced due to live reading of 0.7kW Reply: Allocation updated from '1S to V Op-Ex' as already have allocation entries for 1T and 1V. Original allocation 2.25kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW
Note on P240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 32.8A, so 4.5kW allocation reduced by 1.8kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW
Note on R240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 8kW allocation reduced due to live reading of 6.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.6kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW Reply: 4kW allocation reduced due to live reading of 3.7kW
Note on T240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Original allocation 3kW (total cab 6kW), reduced to 0.675 after cab measured as 4.65kW
Note on X240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 1.1kW Reply: Allocation should be 2.25kW, remaining allocation value updated Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW
Note on Z240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 1.3kW Reply: Allocation should be 2.25kW, remaining allocation value updated Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW
Note on AB240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As per glen advise 2KW power is allocated for this live rack
Note on J241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 3.1kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 2.5kW allocation reduced due to live reading of 1kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 1.2kW Reply: 2.5kW allocation reduced due to live reading of 0.9kW Reply: 2.5kW allocation reduced due to live reading of 1KW Reply: 2.5kW allocation reduced due to live reading of 0.9KW
Note on L241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocated, live so halved to 2.5kw
Note on N241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 79A, so 13.5kW allocation reduced by 4.3kW Reply: 6.75kW allocation reduced due to live reading of 0.7kW Reply: Allocation updated from '1S to V Op-Ex' as already have allocation entries for 1T and 1V. Original allocation 2.25kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.7kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW Reply: 2.25kW allocation reduced due to live reading of 0.6kW
Note on P241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 32.8A, so 4.5kW allocation reduced by 1.8kW Reply: 2.25kW allocation reduced due to live reading of 0.9kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 0.9kW Reply: 2.25kW allocation reduced due to live reading of 0.9kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 2.25kW allocation reduced due to live reading of 1.1kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.4kW
Note on R241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 8kW allocation reduced due to live reading of 6.6kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.4kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW Reply: 4kW allocation reduced due to live reading of 3.5kW
Note on T241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Original allocation 3kW (total cab 6kW), reduced to 0.675 after cab measured as 4.65kW
Note on X241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 1.2kW Reply: Allocation should be 2.25kW, remaining allocation value updated Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW
Note on Z241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 1.2kW Reply: Allocation should be 2.25kW, remaining allocation value updated Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.2kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW Reply: 2.25kW allocation reduced due to live reading of 1.3kW
Note on AB241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As per glen advise 2KW power is allocated for this live rack
Note on N242: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1x N9K - 337W - 2 feeds 1x ISR4331 - 42W - 1 feed 2x QB500 - 1207W - 4 feeds
Note on N243: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1x N9K - 337W - 2 feeds 1x ISR4331 - 42W - 1 feed 2x QB500 - 1207W - 4 feeds
Note on I245: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ciena 6500-14 slot[1.5 KW]new rack has been planned- CPL Removal project ORMT_SAP_240123_21_Y850155
Note on J248: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining
Note on L249: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional power has been added under ORMT_SAP_240508_11_Y854105
Note on J250: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining Reply: 2.4kW reduced by 0.7kW for card infill, 1.7kW remaining
Note on J252: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW reduced by 2.6kW estimated load from average of iPDU readings at other sites, 2.4kW remaining

## DC Dist Allocations
Dist (new dist added to bottom of list) | System | Site | Site copy | Load A | Load B | Reading Date | Max A | Max B | 100 | 80 | 63 | 40 | 20 | Spare Positions | Total Allocated Load A | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Allocated Load kW | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Comment ORMT Ref Project Ref Suite & Rack Ref Initials | Total Allocated kW DC Dist | Total Allocated A DC Dist | Allocated Load kW Site check | Allocated Load A Site check | Updated A | Updated B
CAMN02_SEC_WALL_CBDB_01 | CAMN02;DC SYS01 | CAMN02 | CAMN02 | 0 | 0 | 0 | 300 | 300 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CAMN02_SEC_WALL_CBDB_02 | CAMN02;DC SYS01 | CAMN02 | CAMN02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 2 | 0 | 2 | 20.8333 | DE09 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 10.4167 | 10.4167
CAMN02_SYS01_PER_01 | CAMN02;DC SYS01 | CAMN02 | CAMN02 | 0 | 0 | 0 | 300 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CAMN41_SEC_CBDB_BC01 | CAMN41;DC SYS01 | CAMN41 | CAMN41 | 40 | 40 | 2021-02-16 | 300 | 300 | 8 | 10 | 1 | 0 | 0 | 17 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 40
CFDTN1_SEC_WALL_CBDB_1 | CFDTN1;DC SYS01 | CFDTN1 | CFDTN1 | 0 | 0 | 2023-05-09 | 50 | 50 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CFDTN1_SEC_WALL_CBDB_2 | CFDTN1;DC SYS01 | CFDTN1 | CFDTN1 | 0 | 0 | 2021-03-03 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CFDTN1_SEC_WALL_CBDB_3 | CFDTN1;DC SYS01 | CFDTN1 | CFDTN1 | 0 | 0 | 2021-03-03 | 300 | 300 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CFDTN1_SEC_WALL_CBDB_4 | CFDTN1;DC SYS01 | CFDTN1 | CFDTN1 | 0 | 0 | 2023-05-09 | 375 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CFDTN1_SYS01_PER_01 | CFDTN1;DC SYS01 | CFDTN1 | CFDTN1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
KLNN01 DCDB01 | KLNN01;DC SYS01 | KLNN01 | KLNN01 | EOS ONLY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
NRWN51_SEC_CBDB_BC01 | NRWN51;DC SYS01 | NRWN51 | NRWN51 | 20 | 20 | 2020-10-14 | 300 | 300 | 10 | 6 | 4 | 0 | 0 | 20 | 104.1667 | BC07 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 72.0833 | 72.0833
NRW TN1_SEC_CBDB_P01 | NRWTN1;DC SYS01 | NRWTN1 | NRWTN1 | 0 | 0 | 0 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
NRW TN1_SEC_WALL_CBDB1 | NRWTN1;DC SYS01 | NRWTN1 | NRWTN1 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
NRW TN1_SEC_WALL_CBDB2 | NRWTN1;DC SYS01 | NRWTN1 | NRWTN1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
NRWTN1_SYS01_PER01 | NRWTN1;DC SYS01 | NRWTN1 | NRWTN1 | 0 | 0 | 0 | 300 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
PTBTN1_SEC_DD770_DE16 | PTBTN1;DC SYS01 | PTBTN1 | PTBTN1 | 85 | 85 | 2023-06-19 | 300 | 300 | 0 | 2 | 0 | 10 | 9 | 0 | 62.5 | BC7 Alcatel 7210 | 2 | A02 BT Utility | 1 | [27 empty] | 3 | 62.5 | 0 | 0 | 116.25 | 116.25
PTBTN1_SEC_DD770_JH16 | PTBTN1;DC SYS01 | PTBTN1 | PTBTN1 | 100 | 105 | 2023-06-19 | 300 | 300 | 5 | 1 | 1 | 10 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 105
WTT_SEC_CBDB_01 - ignore | WTT;DC SYS01 | WTT | WTT | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WTT_SEC_CBDB_02 - ignore | WTT;DC SYS01 | WTT | WTT | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8333 | SR02 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 10.4167 | 10.4167
WTT_SEC_DCDB_CD10 | WTT;DC SYS01 | WTT | WTT | 25 | 25 | 2023-05-10 | 300 | 300 | 0 | 1 | 5 | 2 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
BFTN03 - Ignore this line | BFTN03;DC SYS01 | BFTN03 | BFTN03 | No records | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3333 | 6500-14 B08 | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | #VALUE! | 41.6667
ACTN01_PDU1A_B | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 61.8 | 62.5 | 2024-04-05 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 218.75 | AS/AT19 RA | 1.8 | AS/AT13-17 Op-Ex | 5.3 | ASAT11 Alcatel 7210 | 1.6 | ASAT12 Alcatel 7210 | 1.8 | [23 empty] | 10.5 | 218.75 | 0 | 0 | 171.175 | 171.875
ACTN01_SEC_CBDB_ALAM1_04 - CAPPED - Do not Allocate | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 260 | 250 | 2020-12-17 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 260 | 250
ACTN01_SEC_DD770_ACAD1_01 | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 100 | 100 | 2023-06-01 | 300 | 300 | 1 | 0 | 0 | 17 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
ACTN01_SEC_DD770_AEAF1_02 | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 140 | 190 | 2023-06-01 | 300 | 300 | 3 | 6 | 0 | 3 | 12 | 0 | 41.6667 | AL08 Cisco ASA-5585 | 1 | AG 3a BT EAD | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 160.8333 | 210.8333
ACTN01_SEC_DD770_AGAH1_03 | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 110 | 120 | 2023-06-07 | 300 | 300 | 5 | 6 | 0 | 2 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 110 | 120
ACTN01_SEC_DD770_ATAS1_05 | ACTN01;DC SYS01 | ACTN01 | ACTN01 | 74 | 73 | 2023-06-01 | 200 | 200 | 0 | 0 | 4 | 0 | 0 | 23 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 74 | 73
BHWCN1_SYS_DCDB_WALL | BHWCN1;DC SYS01 | BHWCN1 | BHWCN1 | 90A | 90A | 2017-03-22 | 375 | 375 | 0 | 7 | 1 | 0 | 1 | 0 | 20.8333 | B05 MSP7750 PE | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | #VALUE! | #VALUE!
BTFTB1_PDU1A_B | BTFTB1;DC SYS02 | BTFTB1 | BTFTB1 | 310.6 | 284.6 | 2024-04-17 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 736.4583 | S27 PX | 1 | AA07 Netflix | 1.8 | AA06 Akamai | 1.3 | AB02-06 Op-Ex | 10.9 | AA9 BNG | 1.8 | AA3 Facebook | 2.65 | AA10 Google | 2.2 | AZ10 Alcatel 7210 | 2 | AB7 QWILT | 2.4 | Nokia ESA400 AA11 | 2.9 | AA02 RA | 2.5 | AB1 Waveserver | 3.9 | [7 empty] | 35.35 | 736.4583 | 0 | 0 | 678.8292 | 652.8292
Capped_BTFTB1_SEC_DCDB_C11 | BTFTB1;DC SYS01 | BTFTB1 | BTFTB1 | 250 | 250 | 2021-03-03 | 300 | 300 | 0 | 0 | 0 | 0 | 6 | 13 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 250 | 250
Capped_BTFTB1_SEC_DCDB_Suite K14 | BTFTB1;DC SYS01 | BTFTB1 | BTFTB1 | 250 | 250 | 2021-03-03 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 250 | 250
CHTN07_SEC_DD770_00_AB09 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 50 | 50 | 2023-02-09 | 300 | 300 | 5 | 0 | 6 | 16 | 12 | 0 | 52.0833 | BT EAD AMAN07 | 1 | 7750 12B AN10 | 1.5 | [27 empty] | 2.5 | 52.0833 | 0 | 0 | 76.0417 | 76.0417
CHTN07_SEC_DD770_01_CD09 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 90 | 100 | 2023-05-25 | 300 | 300 | 1 | 2 | 0 | 20 | 12 | 0 | 291.6667 | EF03 Alcatel 7210 | 2 | EF04 Alcatel 7210 | 2 | EF07 Alcatel 7210 | 2 | EF04 Alcatel 7210 | 2 | EF05 Alcatel 7210 | 2 | EF05 Alcatel 7210 | 2 | EF05 Alcatel 7210 | 2 | [17 empty] | 14 | 291.6667 | 0 | 0 | 235.8333 | 245.8333
CHTN07_SEC_DD770_02_JK01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 80 | 80 | 2023-02-09 | 300 | 300 | 4 | 0 | 0 | 4 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
CHTN07_SEC_DD770_03_YZ01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 60 | 60 | 2023-02-09 | 300 | 300 | 4 | 4 | 3 | 6 | 0 | 20 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
CHTN07_SEC_DD770_06_WALL_AM AN | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 10 | 10 | 2023-02-09 | 250 | 250 | 0 | 0 | 4 | 4 | 6 | 29 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 10
CHTN07_SEC_DD770_AA AB01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 180 | 180 | 2023-02-09 | 300 | 300 | 7 | 0 | 5 | 0 | 0 | 17 | 22.9167 | Ciena 6500 AA AB 02 | 1.1 | [29 empty] | 1.1 | 22.9167 | 0 | 0 | 191.4583 | 191.4583
CHTN07_SEC_DD770_AK00 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 320 | 320 | 2023-02-09 | 300 | 300 | 3 | 2 | 0 | 0 | 5 | 10 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 320 | 320
CHTN07_SEC_DD770_NP01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 50 | 40 | 2021-09-30 | 300 | 300 | 1 | 0 | 0 | 0 | 4 | 43 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 40
CHTN07_SEC_DD770_UV01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 120 | 120 | 2023-02-09 | 300 | 300 | 0 | 0 | 11 | 0 | 3 | 31 | 20.8333 | BT EAD ST04 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 130.4167 | 130.4167
CHTN07_SEC_DD770_WX01 | CHTN07;DC SYS01 | CHTN07 | CHTN07 | 100 | 100 | 2023-02-09 | 300 | 300 | 3 | 0 | 0 | 0 | 3 | 36 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
CHTN07_SEC_WALL_Eaton_AG AH | CHTN07;DC SYS01 | CHTN07 | CHTN07 | N/A | N/A | 2023-02-09 | 300 | 300 | 8 | 0 | 30 | 0 | 0 | 5 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
CHTTN3_PDU1A_B | CHTTN3;DC SYS01A | CHTTN3 | CHTTN3 | 232.7 | 219.2 | 2024-04-18 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 172.9167 |  |  | BD09 RA | 1.3 | BD06 Op-Ex | 2.8 | BD05 Op-Ex | 0.9 | BD04 Op-Ex | 2.4 | BE9 7750 SR7s | 0.9 | [19 empty] | 8.3 | 172.9167 | 0 | 0 | 319.1583 | 305.6583
CHTTN3_SEC_WALL_DCDB_ 02 | CHTTN3;DC SYS01A | CHTTN3 | CHTTN3 | 0 | 0 | 0 | 300 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CHTTN3_SEC_WALL_DCDB_ 04 | CHTTN3;DC SYS01A | CHTTN3 | CHTTN3 | 65 | 75 | 2023-02-10 | 300 | 300 | 0 | 0 | 1 | 1 | 0 | 37 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 65 | 75
CYNTN2_SEC_DD770_BE08_DB1 | CYNTN2;DC SYS01 | CYNTN2 | CYNTN2 | 125 | 125 | 2023-07-03 | 300 | 300 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 125 | 125
CYNTN2_SEC_DD770_BG08_DB2 | CYNTN2;DC SYS01 | CYNTN2 | CYNTN2 | 125 | 126 | 2023-07-03 | 300 | 300 | 0 | 1 | 3 | 6 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 125 | 126
CYNTN2_SEC_DD770_BM02_DB5 | CYNTN2;DC SYS01 | CYNTN2 | CYNTN2 | 150 | 150 | 2023-07-03 | 300 | 300 | 0 | 2 | 1 | 9 | 8 | 0 | 62.5 | E10 BT EAD | 2 | BA05 Alcatel 7210 | 1 | [27 empty] | 3 | 62.5 | 0 | 0 | 181.25 | 181.25
CYNTN2_SEC_DD770_J01_DB3 | CYNTN2;DC SYS01 | CYNTN2 | CYNTN2 | 90 | 90 | 2023-07-03 | 250 | 250 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 90 | 90
Waddon_DCDB | WADN01;DC SYS01 | WADN01 | WADN01 | 22 | 22 | 2016-02-22 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 22 | 22
DKTN08_SEC_DD770_CD01_01 | DKTN08; DC SYS01 | DKTN08 | DKTN08 | 120 | 140 | 2020-10-01 | 300 | 300 | 5 | 6 | 9 | 4 | 9 | 0 | 20.8333 | A04 BT EAD | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 130.4167 | 150.4167
DKTN08_SEC_DD770_EF01_02 | DKTN08; DC SYS01 | DKTN08 | DKTN08 | 80 | 80 | 2020-10-01 | 300 | 300 | 6 | 6 | 11 | 8 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
DKTN08_SEC_DD770_JK01_03 | DKTN08; DC SYS01 | DKTN08 | DKTN08 | 50 | 60 | 2020-10-01 | 300 | 300 | 5 | 5 | 12 | 14 | 11 | 12 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 60
DKTN08_SEC_DD770_LM01_04 | DKTN08; DC SYS01 | DKTN08 | DKTN08 | 150 | 170 | 2020-10-01 | 300 | 300 | 6 | 4 | 0 | 1 | 12 | 0 | 125 | ST05 Alcatel 7210 | 2 | ST05 Alcatel 7210 | 2 | ST07 Alcate 7210 | 2 | [25 empty] | 6 | 125 | 0 | 0 | 212.5 | 232.5
DKTN08_SEC_DD770_QR01_05 | DKTN08; DC SYS01 | DKTN08 | DKTN08 | 150 | 130 | 2020-10-01 | 300 | 300 | 4 | 0 | 0 | 21 | 11 | 0 | 104.1667 | ST04 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 202.0833 | 182.0833
HRWN02_SEC_DD770_CD01 | HRWN02;DC SYS01 | HRWN02 | HRWN02 | 40 | 30 | 2020-10-01 | 300 | 300 | 6 | 2 | 5 | 10 | 11 | 0 | 156.25 | KJ03 RA | 5 | JK04 Alcatel 7210 | 1 | JK04 Alcatel 7210 | 1 | C03 BT EAD[KA7] | 0.5 | [23 empty] | 7.5 | 156.25 | 0 | 0 | 118.125 | 108.125
HRWN02_SEC_DD770_GH01 | HRWN02;DC SYS01 | HRWN02 | HRWN02 | 80 | 100 | 2020-10-01 | 300 | 300 | 1 | 0 | 0 | 11 | 9 | 0 | 41.6667 | G14 BT EAD | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 100.8333 | 120.8333
DCDB _C4. | IODN01;DC SYS01 | IODN01 | IODN01 | 105 | 95 | 2021-01-21 | 300 | 300 | 2 | 0 | 0 | 0 | 2 | 34 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 105 | 95
DCDB _E04 | IODN01;DC SYS01 | IODN01 | IODN01 | 25 | 25 | 2020-11-26 | 300 | 300 | 2 | 0 | 0 | 2 | 2 | 55 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
DCDB _G04 | IODN01;DC SYS01 | IODN01 | IODN02 | 125 | 120 | 2020-11-26 | 300 | 300 | 2 | 0 | 0 | 1 | 2 | 37 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 125 | 120
DCDB _J04 | IODN01;DC SYS01 | IODN01 | IODN01 | 5 | 25 | 2020-11-26 | 300 | 300 | 0 | 0 | 0 | 1 | 2 | 49 | 416.6667 | HJ05 RA | 5 | HJ08 Opex | 4.5 | MN02 Op-ex | 4.5 | MN01 BT EAD | 1 | MN02 RLS&WAVESERVER | 5 | [21 empty] | 20 | 416.6667 | 0 | 0 | 213.3333 | 233.3333
IGNN01_SEC_CBDB_EF11 | IGNN01;DC SYS01 | IGNN01 | IGNN01 | 97 | 103 | 2021-02-02 | 300 | 300 | 0 | 0 | 0 | 0 | 3 | 0 | 125 | JK14 RA | 5 | GH17 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 159.5 | 165.5
IGNN01_SEC_DD770_ CD01 | IGNN01;DC SYS01 | IGNN01 | IGNN01 | 75 | 50 | 2021-07-07 | 300 | 300 | 6 | 6 | 0 | 12 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 75 | 50
IGNN01_SEC_DD770_ CD23 | IGNN01;DC SYS01 | IGNN01 | IGNN01 | 60 | 40 | 2021-02-02 | 300 | 300 | 6 | 4 | 4 | 20 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 40
IGNN01_SEC_DD770_ GH01 | IGNN01;DC SYS01 | IGNN01 | IGNN01 | 110 | 150 | 2021-02-02 | 300 | 300 | 6 | 0 | 1 | 9 | 12 | 0 | 20.8333 | JK13 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 120.4167 | 160.4167
LSWN01_SEC_DD770_DE01_03 | LSWN01;DC SYS01 | LSWN01 | LSWN01 | 160 | 150 | 2021-04-08 | 300 | 300 | 2 | 3 | 0 | 19 | 9 | 0 | 41.6667 | DE09 Alcatel 7210 | 1 | DE09 Alcatel 7210 | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 180.8333 | 170.8333
LSWN01_SEC_DD770_FG01_02 | LSWN01;DC SYS01 | LSWN01 | LSWN01 | 40 | 40 | 2024-02-06 | 300 | 300 | 1 | 1 | 0 | 21 | 12 | 0 | 135.4167 | GF06 Alcatel7210 sas x | 1 | F03 Ciena 6500-14 slot | 5.5 | [27 empty] | 6.5 | 135.4167 | 0 | 0 | 107.7083 | 107.7083
LSWN01_SEC_DD770_JH01_01 | LSWN01;DC SYS01 | LSWN01 | LSWN01 | 65 | 70 | 2021-04-08 | 300 | 300 | 6 | 0 | 0 | 16 | 6 | 0 | 83.3333 | RS07 polatis | 2 | RS08 Polatis | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 106.6667 | 111.6667
LSWN01_SEC_DD770_PQ01_04 | LSWN01;DC SYS01 | LSWN01 | LSWN01 | 140 | 140 | 2021-04-08 | 300 | 300 | 0 | 0 | 0 | 3 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 140
LSWN02_SEC_DCDB_DC01 | LSWN01;DC SYS01 | LSWN02 | LSWN02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 6 | 6 | 39 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LSWN02_SEC_DCDB_EF01 | LSWN01;DC SYS01 | LSWN02 | LSWN02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 3 | 6 | 6 | 42 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
PRLN02;DC DB;SUITE G | PRLN02;DC SYS01 | PRLN02 | PRLN02 | 35 | 35 | 2020-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | #VALUE! | E03 AWS | 4 | E4 Utility Cab | 1,4 | [27 empty] | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE!
RFDN11_SEC_CBDB_ CD01 | RFDN11;DC SYS01 | RFDN11 | RFDN11 | 16 | 14 | 2020-10-07 | 300 | 300 | 8 | 12 | 1 | 0 | 0 | 20 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 16 | 14
SMHN02_SEC_DD770_JK01_02 | SMHN02;DC SYS01 | SMHN02 | SMHN02 | 140 | 140 | 2021-02-24 | 300 | 300 | 5 | 6 | 9 | 0 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 140
SMHN02_SEC_DD770_LM01_01 | SMHN02;DC SYS01 | SMHN02 | SMHN02 | 140 | 140 | 2021-02-24 | 300 | 300 | 5 | 2 | 12 | 2 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 140
SQYN01_SEC_DD770_BC1 | SQYN01;DC SYS02 | SQYN01 | SQYN01 | 200 | 250 | 2023-02-23 | 300 | 300 | 2 | 1 | 0 | 4 | 7 | 0 | 83.3333 | Alcatel 7210 BE7 | 2 | Alcatel 7210 BE9 | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 241.6667 | 291.6667
SQYN01_SEC_DD770_BL1 | SQYN01;DC SYS03 | SQYN01 | SQYN01 | 80 | 80 | 2023-02-23 | 300 | 300 | 6 | 6 | 0 | 6 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
SQYN01_SEC_DD770_BN1 | SQYN01;DC SYS03 | SQYN01 | SQYN01 | 80 | 80 | 2023-02-23 | 300 | 300 | 6 | 6 | 0 | 12 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
SQYN01_SEC_DD770_BQ1 | SQYN01;DC SYS02 | SQYN01 | SQYN01 | 180 | 180 | 2023-02-23 | 300 | 300 | 6 | 7 | 0 | 6 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 180 | 180
SQYN01_SEC_DD770_BS1 | SQYN01;DC SYS02 | SQYN01 | SQYN01 | 20 | 20 | 2023-02-23 | 300 | 300 | 6 | 12 | 0 | 20 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
SQYN01_SEC_DD770_BV1 | SQYN01;DC SYS03 | SQYN01 | SQYN01 | 80 | 80 | 2023-02-23 | 300 | 300 | 4 | 8 | 0 | 9 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
SQYN01_SEC_DD770_BW1 | SQYN01;DC SYS01 | SQYN01 | SQYN01 | 40 | 40 | 2023-02-23 | 300 | 300 | 4 | 10 | 0 | 19 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 40
SQYN01_SEC_DD770_BY1 | SQYN01;DC SYS01 | SQYN01 | SQYN01 | 40 | 0 | 2023-02-23 | 300 | 300 | 3 | 4 | 0 | 10 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 0
SQYN01_SEC_DD770_DE1 | SQYN01;DC SYS03 | SQYN01 | SQYN01 | 210 | 210 | 2023-02-23 | 300 | 300 | 2 | 0 | 0 | 2 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 210 | 210
SQYN01_SEC_DD770_DN1 | SQYN01;DC SYS01 | SQYN01 | SQYN01 | 60 | 60 | 2023-02-23 | 300 | 300 | 6 | 4 | 6 | 22 | 2 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
SQYN02_PDU1A_B | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 243 | 256.2 | 2024-03-14 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 435.4167 | GB02 RA | 2.5 | GB03 PX | 1 | GB05 Op-ex | 3 | GB07 Op-ex | 2.4 | GB09 Op-Ex | 1.9 | GC02 IGW+WSaI | 0.9 | GC05 Waveserver 5 | 3.2 | GC03 QWILT | 4 | GB10 ESA400 | 2 | [13 empty] | 20.9 | 435.4167 | 0 | 0 | 460.7083 | 473.9083
SQYN02_SEC_DCDB_JJJK07 | SQYN02;DC SYS07 | SQYN02 | SQYN02 | 284 | 275 | 2023-06-01 | 300 | 300 | 0 | 1 | 1 | 1 | 0 | 24 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 284 | 275
SQYN02_SEC_DD770_FA1 | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 70 | 100 | 2023-04-18 | 300 | 300 | 6 | 2 | 0 | 19 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 70 | 100
SQYN02_SEC_DD770_FE1 | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 145 | 165 | 2023-04-18 | 300 | 300 | 6 | 0 | 0 | 19 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 145 | 165
SQYN02_SEC_DD770_GL1 | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 90 | 90 | 2023-04-18 | 300 | 300 | 6 | 5 | 0 | 17 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 90 | 90
SQYN02_SEC_DD770_GR1 | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 130 | 140 | 2023-04-18 | 300 | 300 | 0 | 6 | 0 | 16 | 0 | 0 | 83.3333 | JA6 Netflix | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | 171.6667 | 181.6667
SQYN02_SEC_DD770_HM13 | SQYN02;DC SYS06 | SQYN02 | SQYN02 | 260 | 290 | 2023-04-18 | 300 | 300 | 4 | 4 | 0 | 8 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 260 | 290
SQYN02_SEC_DD770_HP1 | SQYN02;DC SYS06 | SQYN02 | SQYN02 | 180 | 60 | 2023-04-18 | 300 | 300 | 2 | 0 | 0 | 23 | 8 | 0 | 66.6667 | JN04 Juniper SRX 4200 | 1 | JMJL01 EXFO BV-110 | 2.2 | [27 empty] | 3.2 | 66.6667 | 0 | 0 | 213.3333 | 93.3333
SQYN02_SEC_DD770_HS1 | SQYN02;DC SYS06 | SQYN02 | SQYN02 | 190 | 200 | 2023-04-18 | 300 | 300 | 1 | 0 | 0 | 19 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 190 | 200
DCDB PER A. | TELHS2;DC SYS01 | TELHS2 | TELHS2 | 100 | 0 | 2021-03-16 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 0
DCDB PER B. | TELHS2;DC SYS01 | TELHS2 | TELHS2 | 100 | 0 | 2021-03-16 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 0
TELHS1_EXP_SEC_DCDB_14_15_D | TELHS1;DC SYS A;EXT ROOM | TELHS1 | TELHS1 | 140 | 89 | 2023-04-24 | 200 | 200 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 89
TELHS1_DCDB Wallbox. - ignore | TELHS1;DC SYS A;EXT ROOM | TELHS1 | TELHS1 | n/a | n/a | 2021-03-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
TELHS1_SEC_DCDB_14_15_H. | TELHS1;DC SYS A;EXT ROOM | TELHS1 | TELHS1 | 55 | 40 | 2023-04-24 | 200 | 200 | 0 | 0 | 3 | 2 | 0 | 21 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 55 | 40
VHXN02_SEC_DD770_CD1 | VHXN02;DC SYS01 | VHXN02 | VHXN02 | 140 | 135 | 2023-04-17 | 300 | 300 | 4 | 2 | 5 | 0 | 7 | 0 | 62.5 | CD10 ISR 4331 | 2 | CD04 BT EAD | 1 | [27 empty] | 3 | 62.5 | 0 | 0 | 171.25 | 166.25
VHXN02_SEC_DD770_GH1 | VHXN02;DC SYS01 | VHXN02 | VHXN02 | 50 | 60 | 2023-04-17 | 300 | 300 | 6 | 6 | 5 | 13 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 60
VXHINT_SEC_Eaton_BA11 | VHXN02;DC SYS01 | VXHINT | VXHINT | 160 | 160 | 2023-04-17 | 300 | 300 | 0 | 0 | 1 | 0 | 5 | 24 | 145.8333 | DA/DB05 RA | 5 | DA/DB04 Alcatel 7210 | 2 | [27 empty] | 7 | 145.8333 | 0 | 0 | 232.9167 | 232.9167
WAHP03_SEC_CBDB_10_11_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_12_13_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_16_17_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_18_19_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_2_3_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 24 | 35 | 2017-04-04 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 24 | 35
WAHP03_SEC_CBDB_20_21_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 352.7083 | 20B FACEBOOK | 2 | 20C FACEBOOK | 2 | 20/21E QWILT | 2.73 | 20/21F NOKIA7750 SR-7S | 6 | Wavesever20/21G | 4.2 | [21 empty] | 16.93 | 352.7083 | 0 | 0 | 176.3542 | 176.3542
WAHP03_SEC_CBDB_22_23_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_4_5_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 56.875 | [31 empty] | 2.73 | 56.875 | 0 | 0 | 28.4375 | 28.4375
WAHP03_SEC_CBDB_6_7_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WAHP03_SEC_CBDB_8_9_A | WAHP;DC SYS A Tx | WAHP03 | WAHP03 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CAPPED_WAHP06_SEC_CBDB00_1_2_D | WAHP; DC SYS A (Feeds WAHP06) | WAHP06 | WAHP06 | 183 | 175 | 04/04/2024 (Clamp meter readings) | 300 | 300 | 0 | 0 | 11 | 3 | 4 | 0 | 125 | IGW 5/6K | 6 | [29 empty] | 6 | 125 | 0 | 0 | 245.5 | 237.5
CAPPED_WAHP06_SEC_CBDB01_1_2_P | WAHP; DC SYS A (Feeds WAHP06) | WAHP06 | WAHP06 | 275 | 275 | 2021-08-12 | 300 | 300 | 2 | 0 | 6 | 3 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 275 | 275
WAHP06_PDU1_A_B | WAHP; DC SYS A (Feeds WAHP06) | WAHP06 | WAHP06 | 180.7 | 164.9 | 2024-03-14 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 308.3333 | 3Q RA | 2.5 | 1S to V Op-Ex | 7.2 | 3K Op-Ex | 2.6 | PX 5/6Q | 0.8 | 3J WS&RLS | 1.7 | [21 empty] | 14.8 | 308.3333 | 0 | 0 | 334.8667 | 319.0667
WAHP06_SEC_CBDB00_3_4_N | WAHP; DC SYS A (Feeds WAHP06) | WAHP06 | WAHP06 | 328 | 252 | 2022-02-07 | 300 | 300 | 1 | 0 | 0 | 0 | 0 | 19 | 135.4167 | HomeBB DNS 5/6H | 3 | 3Z BNG | 2.5 | 5/6E Netflix | 1 | [25 empty] | 6.5 | 135.4167 | 0 | 0 | 395.7083 | 319.7083
DCDB Details WAIP06. | WAIP;DC SYS01;GND | WAIP06 | WAIP06 | 0 | 0 | 2020-10-21 | 300 | 300 | 4 | 0 | 0 | 2 | 4 | 44 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
DCDB_BTNW01- ADVANCE DC 600 Suite 2D. | BTNW01;DC SYS01 | BTNW01 | BTNW01 | 40 | 30 | 2020-11-26 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 30
DCDB_BTNW01- ADVANCE DC 600 Suite 3D. | BTNW01;DC SYS01 | BTNW01 | BTNW02 | 40 | 30 | 2020-11-26 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 30
BCT - DCDB-Suite IJ01 | BCT;DC SYS01 | BCT | BCT | 30 | 29 | 2023-06-05 | 300 | 300 | 5 | 0 | 3 | 0 | 0 | 41 | 62.5 | IJ05 Alcatel 7210 | 1 | J02 6500-14 | 2 | [27 empty] | 3 | 62.5 | 0 | 0 | 61.25 | 60.25
BCT_SEC_DCDB_WALL | BCT;DC SYS01 | BCT | BCT | 0 | 0 | 2023-06-05 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BCT_SYS_DCDB_WALL - Ignore | BCT;DC SYS01 | BCT | BCT | 0 | 0 | 0 | 300 | 300 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BHMTF1 - DCDB.A - Suite.A-B Rack.10A | BHMTF1;DC SYS A | BHMTF1 | BHMTF1 | 163 | N/A | 2023-02-08 | 300 | N/A | 0 | 0 | 0 | 0 | 0 | 43 | 104.1667 | AB01 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 215.0833 | #VALUE!
BHMTF1 - DCDB.B - Suite.A-B Rack.9A | BHMTF1;DC SYS B | BHMTF1 | BHMTF1 | N/A | 164 | 2023-02-08 | N/A | 300 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 164
BMGV02_SEC_CBDB00_2_3_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB01_6_7_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB02_8_9_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB03_10_11_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB04_12_13_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB05_14_15_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV02_SEC_CBDB06_16_17_A | 0 | BMGV02 | BMGV02 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BMGV03_SEC_CBDB_10_11_B | BMGV03; DC SYS A | BMGV03 | BMGV03 | NO PANEL TO READ | NO PANEL TO READ | 12th Novemeber 2020 | 300 | 300 | 0 | 1 | 2 | 0 | 22 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BMGV03_SEC_CBDB_12_13_B | BMGV03; DC SYS A | BMGV03 | BMGV03 | NO PANEL TO READ | NO PANEL TO READ | 12th Novemeber 2020 | 300 | 300 | 0 | 1 | 0 | 0 | 35 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BMGV03_SEC_CBDB_2_3_B | BMGV03; DC SYS A | BMGV03 | BMGV03 | NO PANEL TO READ | NO PANEL TO READ | 12th Novemeber 2020 | 300 | 300 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BMGV03_SEC_CBDB_6_7_B | BMGV03; DC SYS A | BMGV03 | BMGV03 | NO PANEL TO READ | NO PANEL TO READ | 12th Novemeber 2020 | 300 | 300 | 0 | 0 | 1 | 5 | 19 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BMGV03_SEC_CBDB_8_9_B | BMGV03; DC SYS A | BMGV03 | BMGV03 | NO PANEL TO READ | NO PANEL TO READ | 12th Novemeber 2020 | 300 | 300 | 0 | 0 | 0 | 2 | 15 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BHMN05_SEC_DCDB_AG01 | BHMN05;DC SYS A | BHMN05 | BHMN05 | 260 | 280 | 2023-02-01 | 300 | 300 | 0 | 0 | 0 | 5 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 260 | 280
BHMN05_SEC_WALL_DCDB_A | BHMN05;DC SYS A | BHMN05 | BHMN05 | 120 | 120 | 2023-02-01 | 200 | 200 | 4 | 1 | 1 | 0 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 120 | 120
BHMN05_SEC_WALL_DCDB_B | BHMN05;DC SYS A | BHMN05 | BHMN05 | 95 | 95 | 2023-02-01 | 200 | 200 | 6 | 0 | 0 | 0 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 95 | 95
BHMN05_SEC_WALL_DCDB_C | BHMN05;DC SYS A | BHMN05 | BHMN05 | 90 | 105 | 2023-02-01 | 200 | 200 | 6 | 1 | 0 | 1 | 2 | 0 | 41.6667 | ANAP1 Alcatel 7210 | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 110.8333 | 125.8333
BHMN05_SEC_WALL_DCDB_D | BHMN05;DC SYS A | BHMN05 | BHMN05 | 100 | 120 | 2023-02-01 | 200 | 200 | 0 | 1 | 0 | 0 | 9 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 120
BHMN08_PDU1A_B. | BHMN08;DCSYS03B | BHMN08 | BHMN08 | 125.2 | 154.1 | 2024-04-11 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 339.5833 | D2 PX | 0.9 | D3 RA | 2.6 | D5 Util | 1.8 | C2 Op-Ex | 3.2 | C3 Op-Ex | 1.6 | C5 Op-Ex | 2.6 | C6 WS5 & ai | 3.6 | [17 empty] | 16.3 | 339.5833 | 0 | 0 | 294.9917 | 323.8917
NECCD1 (EATON RACKS)_Suite G 1&2. | NECCD1;DC SYS01 | NECCD1 | NECCD1 | NONE | NONE | 21ST OCTOBER 2020 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
NECCD1_DC-DB (Wall Mounted ). | NECCD1;DC SYS01 | NECCD1 | NECCD1 | NONE | NONE | 21ST OCTOBER 2020 | 200 | 200 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
CELL01 - ADVANCE DC 600 Suite 2C. | CELL01;DC SYS01 | CELL01 | CELL01 | 20 | 20 | 17th December 2020 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
CELL01 - ADVANCE DC 600 Suite 3C. | CELL01;DC SYS01 | CELL01 | CELL02 | 20 | 20 | 17th December 2020 | 300 | 300 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
COV_SEC_DD770_AC01 | COV;DC SYS01a | COV | COV | 100 | 100 | 2023-03-13 | 300 | 300 | 2 | 9 | 0 | 6 | 12 | 0 | 327.0833 | AB04 Opex | 4.5 | AB05 Opex | 4.5 | AB06 Opex | 4.5 | P0 BT EAD | 2.2 | [23 empty] | 15.7 | 327.0833 | 0 | 0 | 263.5417 | 263.5417
COV_SEC_DD770_AJ01 | COV;DC SYS01a | COV | COV | 100 | 100 | 22nd October 2020 | 300 | 300 | 2 | 1 | 0 | 12 | 9 | 0 | 20.8333 | AJ05 Cisco ASA-5585 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 110.4167 | 110.4167
COV_SEC_DD770_RS04 | COV;DC SYS01a | COV | COV | 200 | 200 | 22nd October 2020 | 300 | 300 | 6 | 4 | 0 | 20 | 6 | 0 | 41.6667 | EF1 Alcatel 7210 | 1 | EF1 Alcatel 7210 | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 220.8333 | 220.8333
DBY_SEC_DD770_PQ1 | DBY;DC SYS01 | DBY | DBY | 100 | 100 | 2023-06-28 | 300 | 300 | 5 | 3 | 0 | 11 | 6 | 0 | 20.8333 | TU01 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 110.4167 | 110.4167
EVMN01_DCDIST_GH04 | EVMN01;DC SYS01 | EVMN01 | EVMN01 | 0 | 0 | 5th November 2020 | 300 | 300 | 10 | 10 | 6 | 0 | 0 | 15 | 20.8333 | AB 02 XG210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 10.4167 | 10.4167
EVMN01_SEC_DCDIST_GH02 | EVMN01;DC SYS01 | EVMN01 | EVMN01 | 15 | 15 | 2016-12-16 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 15 | 15
LMSCN2 - DCDB - Suite D and E - Wall Mounted. | LMSCN2;DC SYS01 | LMSCN2 | LMSCN2 | 5 | NONE | 2020-10-15 | 32 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 5 | #VALUE!
LMSCN2 - DCDB - Suite G - Wall Mounted. | LMSCN2;DC SYS01 | LMSCN2 | LMSCN2 | NO METER ON PANEL | NO METER ON PANEL | 2020-10-15 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LCT_PDU1A_B | LCT;DC SYS01 | LCT | LCT | 36.3 | 34.8 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 239.5833 | BA02 RA | 1.1 | BA03 MDCN | 4.9 | BA4 IGW,BA5 IGW | 5.5 | [25 empty] | 11.5 | 239.5833 | 0 | 0 | 156.0917 | 154.5917
LCT_SEC_CBDB#02_NN01 | LCT;DC SYS01 | LCT | LCT | 100 | 100 | 2023-03-29 | 300 | 300 | 3 | 0 | 0 | 0 | 0 | 42 | 20.8333 | NP03 Cisco ASA-5585 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 110.4167 | 110.4167
LCT_SEC_DD770_Q5 | LCT;DC SYS01 | LCT | LCT | 265 | 245 | 2023-03-29 | 300 | 300 | 1 | 3 | 0 | 1 | 7 | 0 | 20.8333 | ST07 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 275.4167 | 255.4167
NGM_SEC _DD770_NN07 | NGM;DC SYS03 | NGM | NGM | 140 | 140 | 2023-03-20 | 300 | 300 | 5 | 0 | 3 | 8 | 6 | 0 | 20.8333 | LLMM01 Alcatel 7210 | 1 | I | [28 empty] | 1 | 20.8333 | 0 | 0 | 150.4167 | 150.4167
NGM_SEC_DD770_U | NGM;DC SYS03 | NGM | NGM | 120 | 120 | 2023-03-20 | 300 | 300 | 6 | 0 | 1 | 8 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 120 | 120
NGMTL1_SEC_ L16 | NGMTL1;DC SYS01 | NGMTL1 | NGMTL1 | 25 | 25 | Supply cable size (sq mm) | 300 | 300 | 0 | 0 | 0 | 0 | 6 | 39 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
BSHN03_SEC_CBDB_CA11 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 100 | 110 | 2023-02-02 | 300 | 300 | 0 | 2 | 10 | 5 | 0 | 25 | 41.6667 | CA17 6500-7 | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 120.8333 | 130.8333
BSHN03_SEC_DD770_AA01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 170 | 180 | 2023-02-02 | 300 | 300 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 170 | 180
BSHN03_SEC_DD770_AC01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 42 | 43 | 2024-01-05 | 300 | 300 | 3 | 0 | 12 | 11 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 42 | 43
BSHN03_SEC_DD770_AE01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 160 | 180 | 2023-02-02 | 300 | 300 | 0 | 0 | 2 | 8 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 160 | 180
BSHN03_SEC_DD770_AG01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 110 | 130 | 2023-02-02 | 300 | 300 | 0 | 0 | 3 | 20 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 110 | 130
BSHN03_SEC_DD770_BA01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 20 | 20 | 2023-02-02 | 300 | 300 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
BSHN03_SEC_DD770_BC01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 20 | 20 | 2023-02-02 | 300 | 300 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
BSHN03_SEC_DD770_BE01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 10 | 20 | 2023-02-02 | 300 | 300 | 6 | 4 | 6 | 21 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 20
BSHN03_SEC_DD770_BG01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 85 | 80 | 2023-02-02 | 300 | 300 | 3 | 1 | 6 | 11 | 11 | 0 | 45.8333 | Virgin media NTE BH18 | 2.2 | [29 empty] | 2.2 | 45.8333 | 0 | 0 | 107.9167 | 102.9167
BSHN03_SEC_DD770_CE01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 15 | 40 | 2023-02-02 | 300 | 300 | 0 | 6 | 4 | 24 | 18 | 0 | 83.3333 | CC12 6500-14 | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | 56.6667 | 81.6667
BSHN03_SEC_DD770_CG01 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 100 | 120 | 2023-02-02 | 300 | 300 | 0 | 3 | 0 | 25 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 120
BSHN03_SEC_DD770_GH14 | BSHN03;DC SYS A | BSHN03 | BSHN03 | 80 | 90 | 2023-02-02 | 300 | 300 | 3 | 0 | 0 | 7 | 10 | 0 | 91.6667 | Cisco 6300 C02 | 2.2 | Cisco 6300 C04 | 2.2 | [27 empty] | 4.4 | 91.6667 | 0 | 0 | 125.8333 | 135.8333
BSHN07_SEC_CBDB_E01 | BSH;DC SYS03;GND | BSHN07 | BSHN07 | 166 | 147 | 2023-02-07 | 227 | 202 | 0 | 0 | 11 | 0 | 0 | 37 | 79.1667 | Facebook | 2 | Google | 1.8 | [27 empty] | 3.8 | 79.1667 | 0 | 0 | 205.5833 | 186.5833
BSHN07_SEC_DD770_LL03 | BSH;DC SYS03;GND | BSHN07 | BSHN07 | 250 | 275 | 2023-02-07 | 300 | 300 | 4 | 1 | 0 | 2 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 250 | 275
BSHN08_PDU1A_B | BSH;DC SYS01;GND | BSHN08 | BSHN08 | 223.9 | 175.5 | 2024-04-16 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 414.5833 | A2 RA | 2.2 | A3 PX | 0.7 | B2 Op-Ex | 3 | B3 Op-Ex | 2.7 | B5 Op-Ex | 2.6 | B6 Op-Ex | 2.9 | Util rack | 2 | Home BB | 3 | A4 Cisco | 0.8 | [13 empty] | 19.9 | 414.5833 | 0 | 0 | 431.1917 | 382.7917
SOLN02_SEC_DD770_DE01 | SOL;DC SYS01 | SOLN02 | SOLN02 | 60 | 60 | 2020-10-13 | 300 | 300 | 5 | 6 | 6 | 11 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
SOLN02_SEC_DD770_GF01 | SOL;DC SYS01 | SOLN02 | SOLN02 | 20 | 30 | 0 | 300 | 300 | 6 | 6 | 1 | 23 | 12 | 0 | 41.6667 | FG03 BT Util | 1 | FG05 Alcatel 7210 | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 40.8333 | 50.8333
SOT_SEC_DCDB_ WALL_Suite GH - Rack 03 | SOT;DC SYS01 | SOT | SOT | 113 | 110 | 2023-06-05 | 300 | 300 | 1 | 0 | 3 | 0 | 0 | 26 | 20.8333 | NP07 Alcatel 7210 SAS-SX | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 123.4167 | 120.4167
SOT_SEC_WALL_DCDB_01_No DCDB found | SOT;DC SYS01 | SOT | SOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SOT_SEC_WALL_DCDB_02_No DCDB found | SOT;DC SYS01 | SOT | SOT | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SOT_SEC_WALL_DCDBA&B_No DCDB found | SOT;DC SYS01 | SOT | SOT | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
WVHTF1_SEC_DCDB.1 - Suite.J Rack.0. | WVHTF1;DCSys01 | WVHTF1 | WVHTF1 | 90 | 90 | 23rd March 2021 | 300 | 300 | 0 | 0 | 6 | 0 | 0 | 24 | 104.1667 | AB06 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 142.0833 | 142.0833
CHDCD1_SEC_CBDB_ D05 | CHDCD1;DC SYS01 | CHDCD1 | CHDCD1 | 40 | 40 | 2023-06-28 | 125 | 125 | 0 | 0 | 5 | 0 | 4 | 34 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 40
DONTN1_DCDB _GH2 | DONTN1;DC SYS01 | DONTN1 | DONTN1 | 90 | 90 | 2020-10-22 | 300 | 300 | 6 | 4 | 0 | 10 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 90 | 90
LDMS13_SYS_DCDB_3J | LDMS13;DC SYS01 A | LDMS13 | LDMS13 | 43 | 58 | 2021-02-25 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 43 | 58
LDSCD1_SEC_DD770_AB1 | LDSCD1;DC SYS01 | LDSCD1 | LDSCD1 | 0 | 0 | 0 | 300 | 300 | 4 | 6 | 10 | 14 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LDSCD1_SEC_WALL_DD770 | LDSCD1;DC SYS01 | LDSCD1 | LDSCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 5 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LDSCD1_SYS_DCDB_01 | LDSCD1;DC SYS01 | LDSCD1 | LDSCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LDSCD1_SYS_DCDB_02 | LDSCD1;DC SYS01 | LDSCD1 | LDSCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LDSCD2_PDU1A_B | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 178.9 | 121.9 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 179.1667 | XY2 RA | 2 | XY03 PX | 0.5 | ABAC02-06 Op-Ex | 2.1 | XY06 Nokia 7750SR7s | 2 | VW04 Alcatel 7210 | 1 | VW05 Alcatel 7210 | 1 | [19 empty] | 8.6 | 179.1667 | 0 | 0 | 268.4833 | 211.4833
LDSCD2_SEC_CBDB_AB1 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 100 | 100 | 2020-10-12 | 300 | 300 | 0 | 0 | 0 | 2 | 6 | 35 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
LDSCD2_SEC_CBDB_CD1 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 260 | 230 | 2021-07-05 | 300 | 300 | 0 | 0 | 0 | 2 | 0 | 17 | 83.3333 | C13 6500-32 | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | 301.6667 | 271.6667
LDSCD2_SEC_CBDB_EF1 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 250 | 250 | 2020-10-12 | 300 | 300 | 0 | 0 | 3 | 0 | 4 | 29 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 250 | 250
LDSCD2_SEC_CBDB_GH1 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 50 | 0 | 2020-10-12 | 300 | 300 | 0 | 0 | 0 | 16 | 9 | 18 | 87.5 | CD06 Juniper SRX 4200 | 1 |  |  | G15 BTOSA | 3.2 | [25 empty] | 4.2 | 87.5 | 0 | 0 | 93.75 | 43.75
LDSCD2_SEC_CBDB_JK1 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 150 | 150 | 2020-10-12 | 300 | 300 | 0 | 0 | 2 | 0 | 0 | 12 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 150 | 150
LDSCD2_SEC_CBDB_TU01 | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 241 | 156 | 2021-10-13 | 300 | 300 | 5 | 0 | 0 | 0 | 0 | 12 | 343.75 | XY05 HPDL360S | 5 | Netflix TU12 | 2.9 | Google TU5 | 1.8 | Facebook TU7 | 5.6 | Facebook TU8 | 1.2 | [21 empty] | 16.5 | 343.75 | 0 | 0 | 412.875 | 327.875
LDSCD2_SEC_CBDB_XY01 (this is actually the iPDU) | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LDSTS1_DCDB Eaton J10 | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | 155 | 155 | 2023-02-17 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 155 | 155
LDSTS1_DCDB Eaton M19 | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | 132 | 129 | 2023-02-17 | 300 | 300 | 1 | 0 | 0 | 0 | 0 | 34 | 222.9167 | H19 RA | 5 | PQ11 Ciena 6500 | 1.5 | P03 BT OSA | 3.2 | H20 Alcatel 7210 | 1 | [23 empty] | 10.7 | 222.9167 | 0 | 0 | 243.4583 | 240.4583
LDSTS1 EOS DA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS EA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS FA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS GA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS HA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS JA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS KA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS LA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS M | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS MA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS N | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
LDSTS1 EOS NA | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | N/A | N/A | 2023-02-17 | 80 | 80 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
IGNORE | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
IGNORE | LDSTS1;DC SYS01 | LDSTS1 | LDSTS1 | 0 | 0 | 0 | 300 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
MDBTD1_EATON DC-DB-1. | MDBTD1;DC SYS01 | MDBTD1 | MDBTD1 | 0.5 | 0.5 | 16/10/2020 | 300 | 300 | 6 | 0 | 0 | 0 | 0 | 37 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0.5 | 0.5
NULTB1_SEC_CBDB_Suite D. | NULTB1;DC SYS01 | NULTB1 | NULTB1 | 40 | 40 | 2021-02-08 | 300 | 300 | 0 | 0 | 14 | 1 | 0 | 32 | 104.1667 | AB05 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 92.0833 | 92.0833
NWCN05_PDU1A_B | NWCN05;DC SYS01 | NWCN05 | NWCN05 | 58.4 | 38.9 | 2024-03-14 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 402.0833 | M01 RA | 1.8 | P01-03 Op Ex | 10.3 | MN02 Alcatel 7210 | 1.7 | E15 IGW, E13 IGW | 5.5 | [23 empty] | 19.3 | 402.0833 | 0 | 0 | 259.4417 | 239.9417
NWCN05_SEC_DD770_AB01 | NWCN05;DC SYS01 | NWCN05 | NWCN05 | 70 | 0 | 2020-09-10 | 300 | 300 | 3 | 0 | 4 | 14 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 70 | 0
NWCN05_SEC_DD770_CD17 | NWCN05;DC SYS01 | NWCN05 | NWCN05 | 80 | 60 | 2020-09-10 | 300 | 300 | 6 | 0 | 4 | 11 | 9 | 0 | 20.8333 | K02,XG210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 90.4167 | 70.4167
SHD_SEC_DD770_AB7 | SHD;DC SYS01 | SHD | SHD | 100 | 100 | 2023-02-14 | 300 | 300 | 2 | 1 | 0 | 10 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
SHD_SEC_DD770_GH00 | SHD;DC SYS01 | SHD | SHD | 110 | 110 | 2023-02-14 | 300 | 300 | 3 | 3 | 0 | 11 | 8 | 0 | 5.2083 | T02 Alcatel 7210 | 0.25 | [29 empty] | 0.25 | 5.2083 | 0 | 0 | 112.6042 | 112.6042
SHD_SEC_WALL_CBDB4 | SHD;DC SYS01 | SHD | SHD | 40 | 45 | 2023-02-14 | 300 | 300 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 45
SNDTM1_PRI_WALL_DIST A3_RECT A | SNDTM1;DC SYS01 | SNDTM1 | SNDTM1 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SNDTM1_PRI_WALL_DIST B2_RECT B | SNDTM1;DC SYS01 | SNDTM1 | SNDTM1 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
TGY_SEC_DD770_D08 | TGY;DC SYSA | TGYN04 | TGYN04 | 25 | 25 | 2023-02-16 | 300 | 300 | 6 | 5 | 6 | 14 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
TGY_SEC_DD770_V1 | TGY;DC SYSA | TGYN04 | TGYN04 | 100 | 100 | 2023-02-16 | 300 | 300 | 0 | 3 | 6 | 24 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
TGY_SEC_WALL_CBDB | TGY;DC SYSA | TGYN04 | TGYN04 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
TGY_SEC_Eaton_BD01_Room5 | TGY;DC SYSA | TGYN04 | TGYN04 | 87 | 87 | 2023-02-16 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 447.9167 | BC01 PX | 8 | BC02 Op-Ex | 4.5 | BC03 Op-Ex | 4.5 | BC04 Op-Ex | 4.5 | [23 empty] | 21.5 | 447.9167 | 0 | 0 | 310.9583 | 310.9583
TGYN02_SEC_DD770_N01 | TGY;DC SYSA | TGYN04 | TGYN04 | 60 | 65 | 2023-02-16 | 300 | 300 | 3 | 6 | 6 | 18 | 12 | 0 | 87.5 | Waveserver 5 AB4 | 4.2 | [29 empty] | 4.2 | 87.5 | 0 | 0 | 103.75 | 108.75
TGYN02_SEC_WALL_DCDB5 | TGY;DC SYSA | TGYN04 | TGYN04 | 40 | 45 | 2023-02-16 | 160 | 160 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 45
TGYN03_SEC_DD770_01 | TGY;DC SYSA | TGYN04 | TGYN04 | 180 | 185 | 2023-02-16 | 300 | 300 | 0 | 1 | 0 | 20 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 180 | 185
TGYN04_SEC_EATON_D04 | TGY;DC SYSA | TGYN04 | TGYN04 | 30 | 30 | 2014-08-18 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 30 | 30
YRK_SEC_DD770_WALL_1 | YRK;DC SYS01 | YRK | YRK | 100 | 95 | 2023-05-03 | 300 | 300 | 3 | 0 | 2 | 10 | 11 | 0 | 20.8333 | LM01 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 110.4167 | 105.4167
YRKTH1_SEC_CBDB_ DE01 | YRKTH1; DC SYS01 | YRKTH1 | YRKTH1 | 25 | 25 | 2023-05-02 | 300 | 300 | 6 | 0 | 1 | 0 | 0 | 40 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
BIFTS1_POWEC_C08 | BIFTS1; DC SYS01 | BIFTS1 | BIFTS1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BPL_SEC_DCDB_F05 | BPL;DC SYS01 | BPL | BPL | 20 | 15 | 2024-02-19 | 300 | 300 | 4 | 0 | 2 | 0 | 0 | 33 | 112.5 | G04 CPL | 1 | DE3 UTILITY RACK | 4.4 | [27 empty] | 5.4 | 112.5 | 0 | 0 | 76.25 | 71.25
CSL_SEC_WALL_DCDB_01 | CSL;DC SYS01 | CSL | CSL | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CSL_SYS01_PER_01 | CSL;DC SYS01 | CSL | CSL | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CSLN13_SEC_CBDB_ BC0 | CSLN13;DC SYS01 | CSLN13 | CSLN13 | 50 | 50 | 2021-04-14 | 300 | 300 | 13 | 10 | 1 | 0 | 0 | 43 | 41.6667 | Ciena 6500 14 D09 | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 70.8333 | 70.8333
CTRTK1_SEC_EATON_BC0 | CTRTK1;DC SYS01 | CTRTK1 | CTRTK1 | 10 | 10 | 2020-11-24 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 10
CTRTS1_SEC_DCDB_GH10 | CTRTS1; DC SYS01 | CTRTS1 | CTRTS1 | 60 | 60 | 2020-10-02 | 300 | 300 | 8 | 4 | 9 | 4 | 0 | 8 | 125 | EF10 RA | 5 | IJ08 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 122.5 | 122.5
EBCTC1_EOS A | ECBTC1; DC SYS01 | EBCTC1 | EBCTC1 | 7.8 | 7.8 | 2022-11-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8333 | D5 Ciena 6500 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 18.2167 | 18.2167
DGS DB1 | DGS;DC SYS01 | DGS | DGS | Not correct form | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
DGS N2K | DGS;DC SYS01 | DGS | DGS | Not correct form | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
KNLTS1_POWEC_PPS25_EXT CAB1 | KNLTS1;DC SYS01 | KNLTS1 | KNLTS1 | 0 | 0 | 0 | 300 | 300 | 9 | 2 | 0 | 0 | 0 | 0 | 20.8333 | GF04 Ciena 6500 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 10.4167 | 10.4167
KNLTS1_POWEC_PPS25_EXT CAB2 | KNLTS1;DC SYS01 | KNLTS1 | KNLTS1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
KNLTS1_POWEC_PPS25_MAIN CAB | KNLTS1;DC SYS01 | KNLTS1 | KNLTS1 | 0 | 0 | 0 | 300 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
LLDTE1_EOS KL00 - ignore | LLDTE1;DC SYS01 | LLDTE1 | LLDTE1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 9 | 177.0833 | PQ09 RA | 5 | Ciena 6500 N08 | 3.5 | [27 empty] | 8.5 | 177.0833 | 0 | 0 | 88.5417 | 88.5417
LPLTB1_SEC_EATON_DC06 | LPLTB1;DC SYS01 | LPLTB1 | LPLTB1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
MCRN11_SEC_CBDB_PQ18 | MCRN11;DC SYS01a | MCRN11 | MCRN11 | 250 | 250 | 26/03/2018 | 300 | 300 | 2 | 0 | 1 | 0 | 0 | 11 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 250 | 250
MCRN11_SEC_DD770_BC01 | MCRN11;DC SYS01a | MCRN11 | MCRN11 | 150 | 150 | 2014-11-07 | 300 | 300 | 2 | 0 | 0 | 3 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 150 | 150
MCRN11_SEC_DD770_HJ01 | MCRN11;DC SYS01a | MCRN11 | MCRN11 | 155 | 155 | 2017-08-01 | 300 | 300 | 2 | 0 | 0 | 15 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 155 | 155
MCRN11_SEC_DD770_HJ19 | MCRN11;DC SYS01a | MCRN11 | MCRN11 | 165 | 145 | 2017-08-01 | 300 | 300 | 2 | 5 | 0 | 7 | 10 | 0 | 83.3333 | KL14 Alcatel 7210 | 2 | KL15 Alcatel 7210 | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 206.6667 | 186.6667
MCRN11_SEC_DD770_PQ01 | MCRN11;DC SYS01a | MCRN11 | MCRN11 | 95 | 95 | 23.02.2017 | 300 | 300 | 0 | 0 | 0 | 12 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 95 | 95
MCRN12_PDU1A_B | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 224.9 | 246.8 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | CC04 to 07 Op-ex | 5 | CC10 RA | 1.4 |  |  | CH2 7750 SR7s | 0.8 | BJ03 Alcatel 7210 SAS SX | 1.6 | BJ05 Alcatel 7210 SAS SX | 1.6 | BJ06 Alcatel 7210 SAS SX | 1.6 | [17 empty] | 12 | 250 | 0 | 0 | 349.9 | 371.8
MCRN12_SEC_CBDB_ Q01_A Feed-Capped | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 55 | 55 | 2021-05-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 55 | 55
MCRN12_SEC_CBDB_ R01_B Feed-Capped | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 55 | 55 | 2021-05-15 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 55 | 55
MCRN12_SEC_CBDB_ALAM01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 245 | 245 | 2021-05-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 245 | 245
MCRN12_SEC_DD770_ACAD01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 135 | 145 | 2021-05-14 | 300 | 300 | 4 | 0 | 0 | 3 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 135 | 145
MCRN12_SEC_DD770_AEAF01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 140 | 140 | 2021-05-14 | 300 | 300 | 1 | 0 | 0 | 13 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 140
MCRN12_SEC_DD770_CD01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 142 | 121 | 2023-01-11 | 300 | 300 | 6 | 6 | 1 | 1 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 142 | 121
MCRN12_SEC_DD770_EF01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 95 | 85 | 2021-05-14 | 300 | 300 | 6 | 1 | 6 | 13 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 95 | 85
MCRN12_SEC_DD770_GH01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 105 | 95 | 2021-05-14 | 300 | 300 | 5 | 0 | 0 | 16 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 105 | 95
MCRN12_SEC_DD770_JK01 | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 90 | 90 | 2021-05-14 | 300 | 300 | 2 | 0 | 4 | 17 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 90 | 90
MCRN12_SEC_Eaton_ BG01_A Feed-Capped | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 250 | NA | 2021-05-14 | 300 | 300 | 2 | 2 | 0 | 0 | 0 | 15 | 93.75 | CA2 AKAMAI | 4.5 | [29 empty] | 4.5 | 93.75 | 0 | 0 | 296.875 | #VALUE!
MCRN12_SEC_Eaton_ BH01_B Feed-Capped | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | NA | 255 | 2020-05-29 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 17 | 93.75 | CA2 AKAMAI | 4.5 | [29 empty] | 4.5 | 93.75 | 0 | 0 | #VALUE! | 301.875
MCRN12_PDU2A_B | MCRN12;DC SYS01 A | MCRN12 | MCRN12 | 196.7 | 194.5 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 512.5 | CH01 IGW+WSaI | 1.2 | CF5Facebook | 1.6 | CF2 Netflix | 1.7 | CF4 Akamai | 1.6 | CF1 Google | 0.9 | CE1 AWS | 2.8 | CCCD2 Wavesever | 3.6 | CC03 SECGW | 2.3 | CH08 AWS | 3 | CF6Facebook | 1.7 | CE2 QWILT | 4.2 | [9 empty] | 24.6 | 512.5 | 0 | 0 | 452.95 | 450.75
MCRCD2_PDU1A_B | MCRCD2;DC SYS02 [Rect 3&4] | MCRCD2 | MCRCD2 | 175.9 | 174.2 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 187.5 | VW2 RA | 1.8 |  |  | TU2 Op-Ex | 2.2 | TU3 Op-Ex | 2 | TU5 Op-Ex | 2.2 | V05 DCN | 0.8 | NOKIA SEGW V6 | [18 empty] | 9 | 187.5 | 0 | 0 | 269.65 | 267.95
SWY_SEC_CBDB_1 | SWY;DC SYS01 | SWY | SWY | 25 | 25 | 2023-06-05 | 300 | 300 | 0 | 9 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
SWY_SEC_CBDB_2 | SWY;DC SYS01 | SWY | SWY | 25 | 25 | 2023-06-05 | 300 | 300 | 0 | 9 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
SWY_SEC_CBDB_4_Suite AH - Rack 5 | SWY;DC SYS01 | SWY | SWY | 60 | 60 | 2023-06-05 | 300 | 300 | 4 | 7 | 0 | 11 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
SWY_SEC_DD770_3_Suite AA - Rack 5 | SWY;DC SYS01 | SWY | SWY | 15 | 15 | 2023-06-05 | 300 | 300 | 6 | 10 | 0 | 22 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 15 | 15
SWY_SEC_DD770_5_Suite AB-AC - Rack 01 | SWY;DC SYS01 | SWY | SWY | 50 | 45 | 2023-06-05 | 300 | 300 | 0 | 1 | 0 | 14 | 0 | 0 | 20.8333 | EF07 BT EAD | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 60.4167 | 55.4167
WTNTK1_SEC_CBDB_J33 | WTNTK1;DC SYS01 | WTNTK1 | WTNTK1 | 100 | 100 | 2023-02-27 | 300 | 300 | 0 | 0 | 5 | 0 | 0 | 37 | 125 | L01 RA | 5 | L02 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 162.5 | 162.5
BDFN02_PDU1A_B | BDFN02;DC SYS01 | BDFN02 | BDFN02 | 150.7 | 167.3 | 2024-04-05 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 416.6667 | BF07 PX | 1.7 | BF08 RA | 1.6 | BF03 Op Ex | 3 | BF04 Op Ex | 2.1 | BF05 Op Ex | 3.5 | BDBE08 Waveserver | 4.5 | AL02 Nokia ESA400 | 2.9 | BF06 PX | 0.7 | [15 empty] | 20 | 416.6667 | 0 | 0 | 359.0333 | 375.6333
BDFN02_SEC_DCDB_AJ01 | BDFN02;DC SYS01 | BDFN02 | BDFN02 | 100 | 100 | 2022-04-28 | 300 | 300 | 12 | 0 | 4 | 1 | 0 | 4 | 62.5 | AGAH03 | 1 | AGAH03 | 1 | BB01 BT EAD | 1 | [25 empty] | 3 | 62.5 | 0 | 0 | 131.25 | 131.25
BDFN02_SEC_DCDB_BD01 | BDFN02;DC SYS01 | BDFN02 | BDFN02 | 325 | 300 | 2022-04-28 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 17 | 83.3333 | BD08 PE7750 | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | 366.6667 | 341.6667
BDFN02_SEC_DD770_AB01 | BDFN02;DC SYS01 | BDFN02 | BDFN02 | 100 | 140 | 2022-05-04 | 300 | 300 | 4 | 2 | 0 | 11 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 140
BDFN02_SEC_DD770_AV01 | BDFN02;DC SYS01 | BDFN02 | BDFN02 | 120 | 170 | 2022-04-28 | 300 | 300 | 1 | 4 | 0 | 3 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 120 | 170
MKSTN1_DCDB_QR7. | MKSTN1;DC SYS01 | MKSTN1 | MKSTN1 | 65 | 65 | 2023-03-13 | 300 | 300 | 5 | 5 | 0 | 22 | 9 | 0 | 20.8333 | QR01 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 75.4167 | 75.4167
MKSTN1_SEC_DD770_GH10 | MKSTN1;DC SYS01 | MKSTN1 | MKSTN1 | 125 | 125 | 2023-03-13 | 300 | 300 | 5 | 3 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 125 | 125
STEDN1_Duvine Power Rack. | STEDN1;DC SYS01 | STEDN1 | STEDN1 | 120 | 0 | 2021-02-12 | 300 | 300 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 120 | 0
BFEC01_SEC_DB00_DCDIST_8A | BFEC01;DC SYS01 | BFEC01 | BFEC01 | 50 | 0 | 2016-02-22 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 0
BFEC01_SEC_DB00_DCDIST_8B | BFEC01;DC SYS01 | BFEC01 | BFEC01 | 50 | 50 | 2016-02-22 | 300 | 300 | 0 | 0 | 42 | 1 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 50
BFEC01_SEC_EATON_C10 | BFEC01;DC SYS01 | BFEC01 | BFEC01 | 70 | 70 | 2024-03-06 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 437.5 | C/CC04 RA | 5 | C/CC 03 Alcatel 7210 | 1 | B11 6500&SAS SX | 5 | B8 RLS & Waveserver | 5 | B9 RLS & Waveserver | 5 | [21 empty] | 21 | 437.5 | 0 | 0 | 288.75 | 288.75
DD770_1_BC01 | BFTN03;DC SYS01 | BFTN03 | BFTN03 | 90 | 90 | 2020-11-25 | 300 | 300 | 0 | 0 | 0 | 9 | 8 | 0 | 197.9167 | BC03 RA | 5 | 6500-14 B08 | 3.5 | BC04 Alcatel 7210 | 1 | [25 empty] | 9.5 | 197.9167 | 0 | 0 | 188.9583 | 188.9583
DD770_2_DE01 | BFTN03;DC SYS01 | BFTN03 | BFTN03 | 45 | 40 | 2024-02-28 | 300 | 300 | 0 | 7 | 2 | 0 | 0 | 0 | 354.1667 | D04 6500-14 | 3.5 | L07 RLS& Waveserver | 5 | L08 RLS& Waveserver | 5 | L06 IGW | 3.5 | [23 empty] | 17 | 354.1667 | 0 | 0 | 222.0833 | 217.0833
DD770_3_FG01 | BFTN03;DC SYS01 | BFTN03 | BFTN03 | Not correct form | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
DD770_4_FG03 | BFTN03;DC SYS01 | BFTN03 | BFTN03 | Not correct form | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
ABN_SEC_DD770_GH02 | ABN;DC SYS01 | ABN | ABN | 30 | 30 | 2016-02-22 | 300 | 300 | 6 | 4 | 3 | 12 | 0 | 17 | 135.4167 | B03a Nokia 7210 | 0.5 | Ciena 6500-14 | 6 | [27 empty] | 6.5 | 135.4167 | 0 | 0 | 97.7083 | 97.7083
ABNTB1_DCDB _CD11 | ABNTB1;DC SYS01 | ABNTB1 | ABNTB1 | 0 | 0 | 2023-03-30 | 300 | 300 | 0 | 0 | 1 | 35 | 0 | 0 | 104.1667 | 6500-14 B09 | 4 | EF1e Alcatel 7210 | 1 | [27 empty] | 5 | 104.1667 | 0 | 0 | 52.0833 | 52.0833
ABNTB1_SYS_RACK2_PANEL A_01 - IGNORE | ABNTB1;DC SYS01 | ABNTB1 | ABNTB1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
ABNTB1_SYS_RACK2_PANEL A_02- IGNORE | ABNTB1;DC SYS01 | ABNTB1 | ABNTB1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
ABNTB1_SYS_RACK3_PANEL B_01- IGNORE | ABNTB1;DC SYS01 | ABNTB1 | ABNTB1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
ABNTB1_SYS_RACK3_PANEL B_02- IGNORE | ABNTB1;DC SYS01 | ABNTB1 | ABNTB1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
ABNTD1 DC DB | ABNTD1;DCSYS01 | ABNTD1 | ABNTD1 | 90 | 83 | 2023-02-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 32 | 104.1667 | 6500-14 E01 | 4 | CD04 Alcatel 7210 | 1 | [27 empty] | 5 | 104.1667 | 0 | 0 | 142.0833 | 135.0833
AYRN01_DCDB_A PPS10_DB1 | AYRN01; DC SYS01 | AYRN01 | AYRN01 | 16 | 0 | 2021-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 16 | 0
AYRN01_DCDB_A PPS10_DB2 | AYRN01; DC SYS01 | AYRN01 | AYRN01 | 0 | 16 | 2021-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 16
DNDN71_SEC_EATON_BC01 | DNDN71; SYS 01 | DNDN71 | DNDN71 | 90 | 90 | 2023-12-13 | 300 | 300 | 0 | 0 | 4 | 0 | 0 | 9 | 208.3333 | DE06 RA | 5 | A04 6500-14 | 4 |  |  |  |  | Marconi MSPP 1684 C04 | 1 | [21 empty] | 10 | 208.3333 | 0 | 0 | 194.1667 | 194.1667
DNDTC1;POWEC987932;DCDB01 | DNDTC1;DCSYS01 | DNDTC1 | DNDTC1 | Not correct form | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8333 | Ciena 6500 7Slot A04 | 0.5 | Ciena 6500 7Slot A04 | 0.5 | [27 empty] | 1 | 20.8333 | 0 | 0 | #VALUE! | 10.4167
DNFNP1_SEC_EATON_C7 | DNFNP1; DC SYS01 | DNFNP1 | DNFNP1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 10 | 10.4167 | B03 Ciena 6500-7 | 0.5 | [29 empty] | 0.5 | 10.4167 | 0 | 0 | 5.2083 | 5.2083
EDBTG1_PDU1A_B | EDBTG1;DC SYSA | EDBTG1 | EDBTG1 | 111.1 | 131.1 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 920.8333 | BA02 RA | 2 | BA03 PX | 1.1 | BB02 Op-EX | 2.5 | BB03 Op-Ex | 2.9 | BA05 Alcatel 7210 | 0.6 | BB04 IGW | 3.6 | BA6 QWILT | 3.5 | BA7 Akami | 5.5 | BA9 FACEBOOK | 5.8 | BA10 FACEBOOK | 5.8 | BA11 Google | 1.9 | BB11 Nokia SecGW | 4 | BB09 Nokia RR 7 Cisco RR | 1 | BB10 Nokia SecGW ESA400 | 4 |  |  |  | 44.2 | 920.8333 | 0 | 0 | 571.5167 | 591.5167
EDBTG1_SEC_DCDB_J02 | EDBTG1;DC SYSA | EDBTG1 | EDBTG1 | 195 | 205 | 2022-03-22 | 300 | 300 | 2 | 9 | 3 | 0 | 0 | 13 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 195 | 205
EDBTG1_SEC_DCDB_D11 | EDBTG1;DC SYSA | EDBTG1 | EDBTG1 | 184 | 181 | 2021-09-14 | 300 | 300 | 0 | 6 | 4 | 0 | 0 | 46 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 184 | 181
EDBTN1_SEC_EATON_EF5 | EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | EDBTN1 | EDBTN1 | 152 | 168 | 2023-03-23 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 48 | 137.5 | A02 Op-EX | 4.6 | AB05 Alcatel 7210 | 2 | [27 empty] | 6.6 | 137.5 | 0 | 0 | 220.75 | 236.75
EDBTN1_DCDB_WALL_A | EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | EDBTN1 | EDBTN1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
EDBTN1_DCDB_WALL_B | EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | EDBTN1 | EDBTN1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
EDBTN1_SEC_EATON_CD15 CAPPED | EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | EDBTN1 | EDBTN1 | 290 | 345 | 2023-03-21 | 300 | 300 | 2 | 0 | 0 | 0 | 0 | 5 | 20.8333 | Security & Misc XY1 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 300.4167 | 355.4167
BTRTP1_SEC_EATON_GF03 | BTRTP1;DC SYS01 | BTRTP1 | BTRTP1 | 10 | 10 | 2014-11-20 | 300 | 300 | 5 | 8 | 0 | 29 | 11 | 0 | #REF! | [31 empty] | #REF! | #REF! | 0 | 0 | #REF! | #REF!
GLWN07_PDU1A_B | GLWN07;DC SYS A | GLWN07 | GLWN07 | 132 | 97.4 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 545.8333 | J22 PX | 2 | CD25 Opex | 2.5 | CD26 Opex | 2.9 | CD22 RA | 2.1 | CD27 Alcatel 7210 | 1.5 | CD30 Ciena 6500 | 3.5 | CD23 PX | 1.2 | Alcatel 7210 CD29 | 1.8 | RLS & WAVESERVER AA22 | 4.1 | WAVESERVER 5 AA23 | 4.6 | [11 empty] | 26.2 | 545.8333 | 0 | 0 | 404.9167 | 370.3167
GLWN07_SEC_DD770_CD01 | GLWN07;DC SYS A | GLWN07 | GLWN07 | 0 | 0 | 0 | 300 | 300 | 1 | 1 | 0 | 2 | 0 | 15 | 83.3333 | Alcatel 7210 CD28 | 2 | Alcatel 7210 CD28 | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 41.6667 | 41.6667
GLWN07_SEC_DD770_EF01 | GLWN07;DC SYS A | GLWN07 | GLWN07 | 0 | 0 | 0 | 300 | 300 | 4 | 0 | 0 | 1 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
GLWN07_SEC_Eaton_CD21 | GLWN07;DC SYS A | GLWN07 | GLWN07 | 78 | 125 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 78 | 125
GLWN07_SEC_DCDB_LM15 - DO NOT USE [CAPPED] | GLWN07;DC SYS A | GLWN07 | GLWN07 | 170 | 170 | 2014-07-14 | 300 | 300 | 4 | 2 | 0 | 1 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 170 | 170
GLWN07_SEC_DD770_JK01- DO NOT USE | GLWN07;DC SYS A | GLWN07 | GLWN07 | 190 | 190 | 2017-02-23 | 300 | 300 | 1 | 1 | 3 | 0 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 190 | 190
GLWTO1_EOS_EF00 | GLWTO1;DC SYS01 | GLWTO1 | GLWTO1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
GLWTO1_EATON_IJ00 | GLWTO1;DC SYS01 | GLWTO1 | GLWTO1 | 0 | 0 | 2021-07-15 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 31 | 145.8333 | KL06 RA | 5 | LK07 Alcatel 7210 | 2 | [27 empty] | 7 | 145.8333 | 0 | 0 | 72.9167 | 72.9167
GLWTW1_DCDB_WALL_1 - IGNORE | GLWTW1;DC SYS01 | GLWTW1 | GLWTW1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
GLWTW1_SEC_EATON DCDB_ EF07B | GLWTW1;DC SYS01 | GLWTW1 | GLWTW1 | 200 | 190 | 2023-03-23 | 300 | 300 | 1 | 0 | 0 | 0 | 0 | 17 | 41.6667 | GH01 Alcatel 7210 | 1 | CD03 Cisco ISR 4331 | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 220.8333 | 210.8333
INVN41_SEC_EATON_CD01 | INVN41;DC SYS01 | INVN41 | INVN41 | 50 | 52 | 2023-07-26 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 145.8333 | EF04 RA | 3 | C03 Ciena 6500-14 SLOT | 4 | [27 empty] | 7 | 145.8333 | 0 | 0 | 122.9167 | 124.9167
LIVN01_SEC_CBDB_AN01 | LIVN01;DC SYS01 | LIVN01 | LIVN01 | 110 | 100 | 2022-10-04 | 300 | 300 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 110 | 100
LIVN01_SEC_DD770_AT05_DCDB4 | LIVN01;DC SYS01 | LIVN01 | LIVN01 | 30 | 30 | 0 | 300 | 300 | 6 | 0 | 0 | 21 | 10 | 0 | 83.3333 | ASAT02 Alcatel 7210 | 2 | ASAT02 Alcatel 7210 | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 71.6667 | 71.6667
PTHTL1_SYS_EATON_DB01 | PTHTL1;DC SYS01 | PTHTL1 | PTHTL1 | 37 | 37 | 2014-07-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3333 | 6500-14 D04 | 4 | [29 empty] | 4 | 83.3333 | 0 | 0 | 78.6667 | 78.6667
STGCD1_SYS_DCDB | STGCD1;DC SYS01 | STGCD1 | STGCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 1 | 2 | 0 | 0 | 0 | 62.5 | 6500-14 G03 | 3 | [29 empty] | 3 | 62.5 | 0 | 0 | 31.25 | 31.25
ASH_SEC_WALL_DCDB_01 | ASH;DC SYS01 | ASH | ASH | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
ASH_SEC_WALL_DCDB_02 | ASH;DC SYS01 | ASH | ASH | 0 | 0 | 0 | 160 | 300 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CBY_SEC_DD770_JK05 | CBY;DC SYS01 | CBY | CBY | 60 | 70 | 2023-06-20 | 300 | 300 | 4 | 6 | 0 | 13 | 11 | 1 | 20.8333 | JK08 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 70.4167 | 80.4167
CBY_SEC_WALL_CBDB | CBY;DC SYS01 | CBY | CBY | 15 | 0 | 2023-06-20 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 15 | 0
FKE_SEC_DD770_AB0. | FKE;DC SYS01 | FKE | FKE | 20 | 20 | 2023-06-20 | 300 | 300 | 6 | 6 | 0 | 19 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
HLWN02_SEC_DD770_EF01_01 | HLWN02;DC SYS01 | HLWN02 | HLWN02 | 80 | 70 | 2022-11-15 | 300 | 300 | 5 | 6 | 4 | 8 | 9 | 0 | 20.8333 | AB04 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 90.4167 | 80.4167
HLWN02_SEC_DD770_JK01_02 | HLWN02;DC SYS01 | HLWN02 | HLWN02 | 32 | 38 | 2022-11-15 | 300 | 300 | 6 | 6 | 0 | 19 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 32 | 38
HHD_SEC_DD770_F0 | HHD;DC SYS01 | HHD | HHD | 135 | 140 | 2023-06-13 | 300 | 300 | 5 | 1 | 0 | 10 | 2 | 0 | 41.6667 | CD02 ALCATEL 7210 SAS SX | 1 | CD08 BT EAD | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 155.8333 | 160.8333
IPWTN1_DCDB _RQ12 | IPWTN1;DC SYS01 | IPWTN1 | IPWTN1 | 60 | 60 | 2023-03-22 | 300 | 300 | 3 | 0 | 3 | 0 | 0 | 33 | 166.6667 | RQ03 RA | 3 | BT OSA ORMT_SAP_220412_32_11408314 | 1 | RQ06 CIENA 6500-14SLOT | 4 | [25 empty] | 8 | 166.6667 | 0 | 0 | 143.3333 | 143.3333
IPWTN1_SEC_DCDB_01 | IPWTN1;DC SYS01 | IPWTN1 | IPWTN1 | N/A | N/A | 2023-03-22 | 300 | 300 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
IPWTN1_SEC_DCDB_04 | IPWTN1;DC SYS01 | IPWTN1 | IPWTN1 | N/A | N/A | 2023-03-22 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
IPWTN1_SYS_DCDB_WALL | IPWTN1;DC SYS01 | IPWTN1 | IPWTN1 | N/A | 0 | 2023-03-22 | 300 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | 0
LTNDN1_SEC_DD770_BB_CC_05 | LTNDN1;DC SYS01 | LTNDN1 | LTNDN1 | 120 | 170 | 2021-03-09 | 300 | 300 | 0 | 6 | 0 | 7 | 9 | 0 | 20.8333 | Alcatel 7210 DE07 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 130.4167 | 180.4167
MDE_SEC_DUVINE DCDB | MDE;DC SYS01 | MDE | MDE | N/A | N/A | 2023-03-21 | 300 | 300 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
MDE_SEC_EATON DCDB | MDE;DC SYS01 | MDE | MDE | 46A | 46A | 2023-03-21 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 48 | 6.25 | E10 ADVA XG210 | 0.3 | [29 empty] | 0.3 | 6.25 | 0 | 0 | #VALUE! | #VALUE!
RCR_SEC_CBDB_GH08 | RCR;DC SYS01 | RCR | RCR | 90 | 95 | 2023-03-21 | 300 | 300 | 3 | 0 | 0 | 0 | 0 | 31 | 125 | LM04 RA | 5 | LM05 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 152.5 | 157.5
RCR_SEC_WALL_CBDB | RCR;DC SYS01 | RCR | RCR | 65 | N/A | 2023-03-21 | 300 | 300 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 65 | #VALUE!
SOSTN1_SEC_DD770_WALL | SOSTN1;DC SYS01 | SOSTN1 | SOSTN1 | 55 | 45 | 2023-05-09 | 300 | 300 | 5 | 0 | 0 | 15 | 11 | 0 | 41.6667 | HJ08 Alcatel 7210 | 1 | KL07 BT EAD | 1 | [27 empty] | 2 | 41.6667 | 0 | 0 | 75.8333 | 65.8333
AZTCD1 POWER SYSTEM 2 DIST | AZTCD1&2;DC SYS01 | AZTCD1 | AZTCD1 | 87.8 | 0 | 2011-01-11 | 300 | 300 | 0 | 0 | 7 | 4 | 11 | 12 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 87.8 | 0
AZTCD1_SEC_EATON DCDB_01_FG07 | AZTCD1&2;DC SYS01 | AZTCD1 | AZTCD1 | 200 | 200 | 2020-07-29 | 300 | 300 | 0 | 0 | 4 | 3 | 0 | 28 | 177.0833 | L08 Nokia1830 | 0.5 | HJ01 RA | 5 | LM04 Alcatel 7210 | 2 | NP07 BT EAD | 1 | [23 empty] | 8.5 | 177.0833 | 0 | 0 | 288.5417 | 288.5417
AZTCD2_SEC_DD770_TU11 | AZTCD1&2;DC SYS01 | AZTCD2 | AZTCD2 | 89 | 78 | 2023-02-20 | 300 | 300 | 4 | 1 | 1 | 12 | 11 | 0 | 20.8333 |  |  |  |  | TU08 Alcatel 7210 | 1 | [25 empty] | 1 | 20.8333 | 0 | 0 | 99.4167 | 88.4167
AZTCD2_SEC_DD770_Q1 | AZTCD1&2;DC SYS01 | AZTCD2 | AZTCD2 | 126 | 122 | 2023-02-20 | 300 | 300 | 4 | 5 | 0 | 7 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 126 | 122
BTLCD1_SYS_H & S Control cubical - ignore line | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BTLCD1 EOS Z | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 0 | 0 | 2023-02-20 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BTLCD1_SEC_DCDB 2_Trident room - Ignore line | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BTLCD1_SEC_DCDB_B | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 110 | 100 | 2023-02-21 | 300 | 300 | 0 | 1 | 0 | 0 | 1 | 0 | 5.2083 | BC09 BT ADVA | 0.25 | [29 empty] | 0.25 | 5.2083 | 0 | 0 | 112.6042 | 102.6042
BTLCD1_SEC_DD770_BB1 | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 20 | 20 | 2023-02-21 | 300 | 300 | 5 | 4 | 0 | 23 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
BTLCD1_SYS _N2K DCDB | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | NA | N/A | 2023-02-21 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
BTLCD1_SYS 2_H & S_DCDB 2B & 2C - Ignore line | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BTLCD1_SYS 3_DCDB_A | BTLCD1;DC SYS01 | BTLCD1 | BTLCD1 | 150 | 160 | 2023-02-21 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 150 | 160
BTLN08_SEC_CBDB_CT1 | BTLN08;DC SYS01 | BTLN08 | BTLN08 | 224 | 223 | 2023-02-20 | 300 | 300 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 224 | 223
BTLN08_SEC_DD770_CA1 | BTLN08;DC SYS01 | BTLN08 | BTLN08 | 150 | 160 | 2023-02-20 | 300 | 300 | 5 | 2 | 0 | 4 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 150 | 160
BTLN08_SEC_DD770_CJ02 | BTLN08;DC SYS01 | BTLN08 | BTLN08 | 160 | 160 | 2023-02-20 | 300 | 300 | 9 | 0 | 5 | 0 | 3 | 1 | 125 | CTCU4 Alcatel 7210 | 3 | CTCU4 Alcatel 7210 | 3 | [27 empty] | 6 | 125 | 0 | 0 | 222.5 | 222.5
BTLCD2_ PRI_DD604_ WALL | BTLCD2;DC SYS01 | BTLCD2 | BTLCD2 | 210 | 0 | 2011-04-01 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 210 | 0
BTLN09_PDU1A_B | BTLN09;DC SYS01 | BTLN09 | BTLN09 | 265.9 | 265.4 | 2024-04-18 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 714.7917 | A02 RA | 1.8 | A04 PX | 1.2 | B02 to 5 Opex | 4.7 | B08 Akamai | 1.9 | B07 IGW | 1.8 | C11 to 26 Amitie | 11.7 | B10 BNG | 1.9 | A7 Facebook | 2.3 | A10 Google | 1.2 | AC11 QWILT | 0.88 | A5 Utility | 0.93 | B13 ESA400 | 4 | [7 empty] | 34.31 | 714.7917 | 0 | 0 | 623.2958 | 622.7958
BDEN02_SEC_DD770_CD01 | BDEN02;DC SYS01 | BDEN02 | BDEN02 | 45 | 55 | 2021-07-27 | 300 | 300 | 6 | 1 | 0 | 9 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 45 | 55
BDEN02_SEC_DD770_QR01 | BDEN02;DC SYS01 | BDEN02 | BDEN02 | 10 | 10 | 2021-07-27 | 300 | 300 | 6 | 6 | 0 | 23 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 10
BDEN06 AB01 DD770 | BDEN06;DC SYS01 | BDEN06 | BDEN06 | 170 | 179 | 2023-05-02 | 300 | 300 | 4 | 2 | 0 | 24 | 11 | 0 | 83.3333 | E05 6500-14 | 2 | A3 Ciena RLS R4 | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 211.6667 | 220.6667
BDEN06 JK01 DD770 | BDEN06;DC SYS01 | BDEN06 | BDEN06 | 80 | 90 | 2023-05-02 | 600 | 600 | 1 | 0 | 3 | 17 | 12 | 0 | 31.25 | AB4 Ciena Waveserver 5 | 1.5 | [29 empty] | 1.5 | 31.25 | 0 | 0 | 95.625 | 105.625
BDEN06 QR01 DD770 | BDEN06;DC SYS01 | BDEN06 | BDEN06 | 10 | 10 | 2023-05-02 | 600 | 600 | 6 | 6 | 6 | 22 | 4 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 10
BDEN07_PDU1A_B | 0 | BDEN07 | BDEN07 | 413.05 | 413.05 | 2024-02-13 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 129.1667 | A 1 to 7 Amitie | 6.2 | [29 empty] | 6.2 | 129.1667 | 0 | 0 | 477.6333 | 477.6333
CDFN02_SEC_CBDB_AB05 | CDFN02;DC SYS01 | CDFN02 | CDFN02 | 120 | 140 | 23rd JUNE 2021 | 300 | 300 | 4 | 1 | 0 | 5 | 6 | 0 | 10.4167 | C05 Nokia 1830 | 0.5 | [29 empty] | 0.5 | 10.4167 | 0 | 0 | 125.2083 | 145.2083
CDFN02_SEC_CBDB_GH06 | CDFN02;DC SYS01 | CDFN02 | CDFN02 | 20 | 20 | 2014-08-15 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 52.0833 | GH5 7210 SAS SX | 2.5 | [29 empty] | 2.5 | 52.0833 | 0 | 0 | 46.0417 | 46.0417
CHMN21_SEC_EATON DCDB1 | CHMN21;DC SYS01 | CHMN21 | CHMN21 | 5 | 5 | 2017-05-16 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 5 | 5
CTNN01_PDU1A_B | CTNN01-DCSYS01A | CTNN01 | CTNN01 | 3.5 | 2.4 | 2024-03-11 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 243.75 | S&T 1 to 6 Amitie | 11.7 | [29 empty] | 11.7 | 243.75 | 0 | 0 | 125.375 | 124.275
CTNN01_SEC_DD770_EF01 | CTNN01-DCSYS01A | CTNN01 | CTNN01 | 60 | 50 | 2022-01-10 | 300 | 300 | 6 | 7 | 0 | 14 | 3 | 0 | 20.8333 | CD01 Ciena 6500 R8 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 70.4167 | 60.4167
CTNN01_SEC_DD770_N01 | CTNN01-DCSYS01A | CTNN01 | CTNN01 | 0 | 0 | 2021-07-20 | 300 | 300 | 6 | 6 | 12 | 22 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CKNN03_PDU1A_B | CKNN03-DCSYS01a | CKKN03 | CKKN03 | 0.76 | 3.3 | 2024-04-18 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 243.75 | E&F 1-6 Amitie | 11.7 | [29 empty] | 11.7 | 243.75 | 0 | 0 | 122.635 | 125.175
CKNN03_SEC_DCSYS - IGNORE | CKNN03-DCSYS01a | CKNN03 | CKNN03 | 0 | 0 | 2021-07-05 | NOT SPECIFIED | NOT SPECIFIED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CKNN03_SEC_DD770_CD01 | CKNN03-DCSYS01a | CKNN03 | CKNN03 | 30 | 40 | 2023-06-12 | 300 | 300 | 5 | 6 | 2 | 18 | 10 | 0 | 20.8333 | CD5 Ciena 6500 R8 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 40.4167 | 50.4167
DVSTB1_DCDB | DVSTB1; DC SYS01 | DVSTB1 | DVSTB1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
EXR_SEC_DD770_ JK12 | EXR;DC SYS01 | EXR | EXR | 90 | 90 | 2023-03-14 | 300 | 300 | 5 | 5 | 0 | 10 | 9 | 0 | 62.5 | PN02 Utility Cab | 2 | LM06 BT OSA NTE | 1 | [27 empty] | 3 | 62.5 | 0 | 0 | 121.25 | 121.25
EXRN03_PDU1A_B | EXRN03-DCSYSa | EXRN03 | EXRN03 | 1.2 | 2.7 | 2024-03-11 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 243.75 | J&K 1-6 Amitie | 11.7 | [29 empty] | 11.7 | 243.75 | 0 | 0 | 123.075 | 124.575
FRNN03_PDU1A_B | FRNN03-DCSYS01a | FRNN03 | FRNN03 | 0 | 4.4 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 243.75 | G&H 1 to 6 Amitie | 11.7 | [29 empty] | 11.7 | 243.75 | 0 | 0 | 121.875 | 126.275
FRNN03_DC SYS01A & 01B_EF09 | FRNN03-DCSYS01a | FRNN03 | FRNN03 | 0 | 0 | 2021-03-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
FRNN03_SEC_DD770_CD1 | FRNN03-DCSYS01a | FRNN03 | FRNN03 | 20 | 20 | 2021-07-22 | 300 | 300 | 6 | 4 | 8 | 20 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
OKNN01_PDU1A_B | OKNN01-DCSYS01a | OKNN01 | OKNN01 | 27.3 | 19.5 | 2024-03-14 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | G06 RA | 2.5 | J&K 1 to 6 Amitie | 11.9 | [27 empty] | 14.4 | 300 | 0 | 0 | 177.3 | 169.5
OKNN01_SEC_DD770_CD01 | OKNN01-DCSYS01a | OKNN01 | OKNN01 | 40 | 20 | 2021-07-21 | 300 | 300 | 6 | 7 | 0 | 19 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 20
PLY_PDU1A_B | PLY-DCSYS01a | PLY | PLY | 11.4 | 0 | 2024-04-04 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 422.9167 | S02 RA | 4.6 | W&X 1 to 6 Amitie | 11.9 | ST03 Utility Cab | 3.8 | [25 empty] | 20.3 | 422.9167 | 0 | 0 | 222.8583 | 211.4583
PLY_SEC_DD770_EF12 | PLY-DCSYS01a | PLY | PLY | 100 | 25 | 2023-03-14 | 300 | 300 | 0 | 0 | 3 | 14 | 10 | 0 | 20.8333 | EF09 BT NTE | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 110.4167 | 35.4167
PLY_SEC_DD770_UV01 | PLY-DCSYS01a | PLY | PLY | 55 | 50 | 2023-03-14 | 300 | 300 | 6 | 0 | 1 | 22 | 11 | 1 | 20.8333 | UV07 Ciena 6500 R8 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 65.4167 | 60.4167
PCOTN1_SEC_DD770_XW01_7 | PCOTN1;DC SYS A;GEMINI | PCOTN1 | PCOTN1 | 60 | 45 | 2023-05-24 | 300 | 300 | 4 | 2 | 0 | 20 | 8 | 0 | 83.3333 | AC03 6500-7 | 2 | TU07 Polatis | 2 | [27 empty] | 4 | 83.3333 | 0 | 0 | 101.6667 | 86.6667
PCOTN1_SEC_WALL_CBDB_2 | PCOTN1;DC SYS A;FLAG | PCOTN1 | PCOTN1 | 10 | 20 | 2023-05-24 | 300 | 300 | 0 | 5 | 0 | 0 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 20
PCOTN1 DCDB 3 WALL MOUNTED | PCOTN1;DC SYS A;GEMINI | PCOTN1 | PCOTN1 | 15 | 0 | 2023-05-24 | 600 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 15 | 0
PCOTN1 DCDB 4 WALL MOUNTED | PCOTN1;DC SYS A;GEMINI | PCOTN1 | PCOTN1 | 25 | 0 | 2023-05-24 | 600 | 0 | 0 | 14 | 0 | 0 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 0
PCOTN1 DCDB 5 WALL MOUNTED | PCOTN1;DC SYS A;GEMINI | PCOTN1 | PCOTN2 | 10 | 0 | 2023-05-24 | 600 | 0 | 0 | 3 | 0 | 0 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10 | 0
PCOTN1 DCDB 6 WALL MOUNTED | PCOTN1;DC SYS A;GEMINI | PCOTN1 | PCOTN3 | 0 | 0 | 2023-05-24 | 600 | 0 | 0 | 3 | 0 | 0 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
PCOTN1_WALL_CBDB_1 | PCOTN1;DC SYS A;FLAG | PCOTN1 | PCOTN4 | 80 | 80 | 2023-05-24 | 300 | 300 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 80
SDNN06_PDU1A_B | SDNN06;DC SYS03 | SDNN06 | SDNN06 | 159 | 146.3 | 2024-03-14 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 302.0833 | Z11 RA | 2.4 | Z12 PX | 0.7 | WX10 Op-EX | 2.1 | WX12 Op-EX | 0.7 | WX9 Op-EX | 1.3 | UV1 Waveserver | 3.3 | CD02 ESA400 | 4 | [17 empty] | 14.5 | 302.0833 | 0 | 0 | 310.0417 | 297.3417
SDNN06_SEC_CBDB_QR16 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 200 | 200 | 2023-03-29 | 300 | 300 | 3 | 1 | 7 | 3 | 0 | 4 | 312.5 | UV4 MSP7750 PE | 6 | V6 Ciena 5410 | 3 | V7 Ciena 6500 | 3 | V8 iena 6500 | 3 | [23 empty] | 15 | 312.5 | 0 | 0 | 356.25 | 356.25
SDNN06_SEC_CBDB_UV16 | SDNN06;DC SYS03 | SDNN06 | SDNN06 | 245 | 245 | 2023-03-24 | 300 | 300 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 245 | 245
SDNN06_SEC_DD770_CD1 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 160 | 160 | 2022-10-10 | 300 | 300 | 4 | 4 | 0 | 9 | 8 | 0 | 239.5833 | CD03 Alcatel 7210 | 2 | CD05 Alcatel 7210 | 2 | CD2 Nokia 7750 SR12e ESA | 7.5 | [25 empty] | 11.5 | 239.5833 | 0 | 0 | 279.7917 | 279.7917
SDNN06_SEC_DD770_GH16 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 20 | 20 | 2022-10-10 | 300 | 300 | 6 | 4 | 0 | 24 | 11 | 0 | 104.1667 | YZ15 Home BB | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 72.0833 | 72.0833
SDNN06_SEC_DD770_LM1 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 160 | No reading | 2022-10-10 | 300 | 300 | 1 | 2 | 0 | 9 | 6 | 0 | 10.4167 | Nokia ILA M12 | 0.5 | [29 empty] | 0.5 | 10.4167 | 0 | 0 | 165.2083 | #VALUE!
SDNN06_SEC_DD770_QR1 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 30 | No reading | 2022-10-10 | 300 | 300 | 6 | 6 | 0 | 10 | 9 | 0 | 250 | QR03 to 09 Amitie | 12 |  |  |  |  | 0 | [24 empty] | 12 | 250 | 0 | 0 | 155 | #VALUE!
SDNN06_SEC_DD770_WX1 | SDNN06;DC SYS02 | SDNN06 | SDNN06 | 100 | 100 | 2022-10-10 | 300 | 300 | 3 | 2 | 0 | 16 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
SDN_SEC_DD770_GH00 | SDN;DC SYS01 | SDN | SDN | 110 | 100 | 2021-06-15 | 300 | 300 | 6 | 4 | 0 | 9 | 11 | 30 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 110 | 100
SDN_SEC_DD770_Z02 | SDN;DC SYS01 | SDN | SDN | 0 | 0 | 2021-06-15 | 300 | 300 | 6 | 10 | 0 | 18 | 11 | 45 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
DCDB @ c08 | SDNN11;DC SYS01 | SDNN11 | SDNN11 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SDNN13_SEC_EATON_ WALL_New | SDNN13;DC SYS01 | SDNN13 | SDNN13 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 28 | 97.9167 | Google | 1.8 | Netflix | 2.9 | [27 empty] | 4.7 | 97.9167 | 0 | 0 | 48.9583 | 48.9583
TNTTN1_PDU1A_B | TNTTN1;DC SYS01 | TNTTN1 | TNTTN1 | 10.2 | 5.3 | 2024-04-04 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 314.5833 | K&L 1-6 Amitie | 11.7 | E11 Utility Cab | 3.4 | [27 empty] | 15.1 | 314.5833 | 0 | 0 | 167.4917 | 162.5917
TNTTN1_SEC_DD770_ GH12 | TNTTN1;DC SYS01 | TNTTN1 | TNTTN1 | 55 | 55 | 2023-03-15 | 300 | 300 | 5 | 4 | 0 | 13 | 0 | 18 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 55 | 55
DC DD770 TRON01 | TRON01;DC SYS01 | TRON01 | TRON01 | 15 | 15 | 2021-07-22 | 300 | 300 | 6 | 8 | 0 | 22 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 15 | 15
BSG_SEC_DD770_BC17_02 | BSG;DC SYS01 | BSG | BSG | 100 | 100 | 2023-05-22 | 300 | 300 | 4 | 0 | 1 | 7 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 100 | 100
BSG_SEC_DD770_HJ16_01 | BSG;DC SYS01 | BSG | BSG | 35 | 35 | 2024-01-04 | 300 | 300 | 6 | 0 | 4 | 20 | 10 | 0 | 83.3333 | FG15 Alcatel 7210 | 3 | FG16 ADVA XG120 | 1 | [27 empty] | 4 | 83.3333 | 0 | 0 | 76.6667 | 76.6667
BTN_SEC_DD770_EF09_02 | BTN-DCSYS01 | BTN | BTN | 120 | 110 | 2023-03-07 | 300 | 300 | 2 | 0 | 0 | 9 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 120 | 110
BTN_SEC_DD770_YZ01_01 | BTN-DCSYS01 | BTN | BTN | 65 | 45 | 2023-03-07 | 300 | 300 | 2 | 0 | 5 | 23 | 12 | 0 | 125 | YZ02 RA | 5 | YZ04 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 127.5 | 107.5
GFDCD1_SEC_DCDB_T0 | GFDCD1;DC SYS01A | GFDCD1 | GFDCD1 | 75 | 100 | 2023-05-22 | 200 | 200 | 3 | 0 | 0 | 0 | 0 | 30 | 289.5833 | HH/HJ 10 Wsai | 4.3 | HH/HJ 11 Wsai | 4.7 | HH/HJ09 RA | 2.6 | AE01 Alcatel 7210 | 1.6 | HH/JJ08 BT OSA | 0.7 | [21 empty] | 13.9 | 289.5833 | 0 | 0 | 219.7917 | 244.7917
GFDCD1_SEC_DD770_M09 | GFDCD1;DC SYS01A | GFDCD1 | GFDCD1 | 140 | 170 | 2023-05-22 | 300 | 300 | 3 | 0 | 1 | 0 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 170
PTMN03_SEC_DD770_BCBD01 | PTMN03;DC SYS01 | PTMN03 | PTMN03 | 30 | 0 | 2020-12-04 | 300 | 300 | 6 | 12 | 0 | 24 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 30 | 0
PTMN03_SEC_DD770_GH01 | PTMN03;DC SYS01 | PTMN03 | PTMN03 | 40 | 40 | 2020-12-04 | 300 | 300 | 6 | 10 | 0 | 18 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 40 | 40
PTMN03_SEC_DD770_LM01 | PTMN03;DC SYS01 | PTMN03 | PTMN03 | 60 | 60 | 2020-12-04 | 300 | 300 | 6 | 11 | 0 | 7 | 1 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
PTMN03_SEC_DD770_QR01 | PTMN03;DC SYS01 | PTMN03 | PTMN03 | 50 | 50 | 2020-12-04 | 300 | 300 | 6 | 0 | 0 | 23 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 50
PTMN03_SEC_DD770_UV01 | PTMN03;DC SYS01 | PTMN03 | PTMN03 | 20 | 20 | 2020-12-04 | 300 | 300 | 6 | 8 | 0 | 23 | 12 | 0 | 125 | UV02 RA | 5 | UV03 Alcatel 7210 | 1 | [27 empty] | 6 | 125 | 0 | 0 | 82.5 | 82.5
SHTN03_SEC_DD770_AD10 | SHTN03;DC SYS02 | SHTN03 | SHTN03 | 210 | 210 | 2024-01-10 | 240 | 240 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 210 | 210
SHTN03_SEC_Eaton_ ANAP0 | SHTN03;DC SYS02 | SHTN03 | SHTN03 | 30 | 27 | 2023-01-11 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 57 | 145.8333 | AN/AP02 RA | 5 | AB03 BT EAD | 1 | AN/AP03 Alcatel 7210 | 1 | [25 empty] | 7 | 145.8333 | 0 | 0 | 102.9167 | 99.9167
DCDB_WKGN01_CD1. | WKGN01;DC SYS01 | WKGN01 | WKGN01 | 25 | 25 | 2020-09-18 | 300 | 300 | 6 | 5 | 12 | 15 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25 | 25
DCDB_WKGN01_EF1. | WKGN01;DC SYS01 | WKGN01 | WKGN01 | 20 | 20 | 0 | 300 | 300 | 6 | 2 | 7 | 23 | 11 | 0 | 104.1667 | EF19 RA | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 72.0833 | 72.0833
ASMN02_SEC_DD770_CD1 | ASMN02;DC SYS01 | ASMN02 | ASMN02 | 20 | 20 | 2020-10-15 | 300 | 300 | 6 | 5 | 7 | 23 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 20 | 20
ASMN02_SEC_DD770_EF1 | ASMN02;DC SYS01 | ASMN02 | ASMN02 | 0 | 0 | 2020-10-15 | 0 | 0 | 0 | 6 | 0 | 24 | 12 | 6 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
BKLN05_SEC_CBDB_BUBV01 | BKLN05;DC SYS03;NEAR CK | BKLN05 | BKLN05 | 225 | 225 | 2024-03-07 | 300 | 300 | 0 | 3 | 0 | 0 | 0 | 26 | 102.2917 | BN14 SKY/AKAMAI | 4.91 | [29 empty] | 4.91 | 102.2917 | 0 | 0 | 276.1458 | 276.1458
BKLN05_SEC_CBDB_BWBX01 | BKLN05;DC SYS02 | BKLN05 | BKLN05 | 100 | 110 | 2021-10-01 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 48 | 183.3333 | Facebook BQBR09 | 2 | Netflix BNBP12 | 2.9 | Google BLBM14 | 3.9 | [25 empty] | 8.8 | 183.3333 | 0 | 0 | 191.6667 | 201.6667
BKLN05_SEC_DD770_ACAD01 | BKLN05;DC SYS02 | BKLN05 | BKLN05 | 120 | 120 | 2021-10-15 | 300 | 300 | 3 | 6 | 0 | 13 | 10 | 7 | 125 | ACAD04 Alcatel 7210 | 2 | ACAD05 Alcatel 7210 | 2 | ACAD06 Alcatel 7210 | 2 | [25 empty] | 6 | 125 | 0 | 0 | 182.5 | 182.5
BKLN05_SEC_DD770_AGAH01 | BKLN05;DC SYS03;NEAR CK | BKLN05 | BKLN05 | 90 | 85 | 2021-10-01 | 300 | 300 | 5 | 5 | 0 | 3 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 90 | 85
BKLN05_SEC_DD770_BABB01 | BKLN05;DC SYS01 | BKLN05 | BKLN05 | 190 | 195 | 2021-10-01 | 300 | 300 | 2 | 3 | 0 | 10 | 12 | 0 | 93.75 | BE/BF 15 Waveserver 5 | 4.5 | [29 empty] | 4.5 | 93.75 | 0 | 0 | 236.875 | 241.875
BKLN05_SEC_DD770_BLBM01 | BKLN05;DC SYS01 | BKLN05 | BKLN05 | 115 | 100 | 2021-10-01 | 300 | 300 | 0 | 0 | 0 | 17 | 6 | 0 | 20.8333 | CC/CD 07 HPE DL 380 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 125.4167 | 110.4167
BKLN05_SEC_DD770_BQBR01 | BKLN05;DC SYS03;NEAR CK | BKLN05 | BKLN05 | 135 | 140 | 2021-10-01 | 300 | 300 | 0 | 0 | 0 | 19 | 8 | 0 | 41.6667 | IGW BNBP7 | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 155.8333 | 160.8333
BKLN05_SEC_DD770_BYBZ01 | BKLN05;DC SYS03;NEAR CK | BKLN05 | BKLN05 | 105 | 110 | 2021-10-04 | 300 | 300 | 4 | 6 | 0 | 11 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 105 | 110
BKLN05_SEC_DD770_CD01 | BKLN05;DC SYS01 | BKLN05 | BKLN05 | 115 | 140 | 2021-10-01 | 300 | 300 | 6 | 2 | 0 | 11 | 11 | 0 | 104.1667 | AKAMAI BE09 | 5 | [29 empty] | 5 | 104.1667 | 0 | 0 | 167.0833 | 192.0833
BKLN05_SEC_DD770_CJCK01 | BKLN05;DC SYS03;NEAR CK | BKLN05 | BKLN05 | 210 | 200 | 2021-10-01 | 300 | 300 | 6 | 1 | 0 | 10 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 210 | 200
BKLN05_SEC_DD770_GH01 | BKLN05;DC SYS01 | BKLN05 | BKLN05 | 135 | 140 | 2021-10-01 | 300 | 300 | 4 | 0 | 0 | 11 | 8 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 135 | 140
BKLN05_SEC_DD770_LM01 | BKLN05;DC SYS01 | BKLN05 | BKLN05 | 10.6 | NA | 2022-09-20 | 300 | 300 | 4 | 0 | 0 | 3 | 4 | 1 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 10.6 | #VALUE!
BKLN05_SEC_DD770_UV01 | BKLN05;DC SYS02 | BKLN05 | BKLN05 | 160 | 165 | 2021-10-01 | 300 | 300 | 0 | 1 | 0 | 19 | 12 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 160 | 165
BKLN05_SEC_DD770_YZ01 | BKLN05;DC SYS02 | BKLN05 | BKLN05 | 85 | 80 | 2021-09-02 | 300 | 300 | 5 | 10 | 0 | 16 | 3 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 85 | 80
BKLN05_DCSYS04-PDU1 | BKLN05-DCSYS04 | BKLN05 Ext | BKLN05 Ext | 366.6 | 108.3 | 2024-04-11 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.5833 |  |  | DF9 7750 SR7s | 1 | DG4 Op-Ex | 0.7 | DG5 Op-Ex | 1 | DG6 Op-Ex | 0.9 | Group DE/DD | 53.5 | [19 empty] | 57.1 | 1189.5833 | 0 | 0 | 961.3917 | 703.0917
BKLN05_DCSYS04-PDU2 | BKLN05-DCSYS04 | BKLN05 Ext | BKLN05 Ext | 217 | 35 | 2024-04-05 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9167 | DG1 RA | 2 | DG2 PX | 0.8 | DF10 Utility Cab | 1.9 | [25 empty] | 4.7 | 97.9167 | 0 | 0 | 265.9583 | 83.9583
BKLN05_DCSYS04-PDU3 | BKLN05-DCSYS04 | BKLN05 Ext | BKLN05 Ext | 262.1 | 55.3 | 2024-04-05 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.25 | VSS DC/DB&DF1,2,4 | 36.2 | DF8 IGW+WSaI | 1.4 |  |  | DG8 M-PE | 0.5 | DG9 M-PE | 0.5 | DC10 DALI | 12.1 | [19 empty] | 50.7 | 1056.25 | 0 | 0 | 790.225 | 583.425
DCDB _DC CUBICLE IN POWER ROOM NEAR BATTERY | DCT;DC SYS01 | DCT | DCT | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6667 | Alcatel & Ciena Y2 | 4.4 | [29 empty] | 4.4 | 91.6667 | 0 | 0 | 45.8333 | 45.8333
FMYN31_SEC_CBDB_ BC01 | FMYN31; DC SYS01 | FMYN31 | FMYN31 | not showing on meter | not showing on meter | 2020-09-10 | 250 | 250 | 10 | 10 | 2 | 0 | 0 | 19 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
DCDB _2B | IVER02; DC SYS01 | IVER02 | IVER02 | 42 | 42 | 2020-10-09 | unknown | unknown | 0 | 0 | 3 | 3 | 3 | 3 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 42 | 42
NBYCD1_SEC_CBDB_F9 | NBYCD1;DC SYS01 | NBYCD1 | NBYCD1 | 60 | 60 | 2023-03-06 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 60 | 60
NBYCD1_SEC_CBDB_GG11 | NBYCD1;DC SYS01 | NBYCD1 | NBYCD1 | 180 | 0 | 2023-03-06 | 300 | 300 | 1 | 0 | 0 | 1 | 0 | 0 | 10.4167 | Nokia ILA E04 | 0.5 | [29 empty] | 0.5 | 10.4167 | 0 | 0 | 185.2083 | 5.2083
POLN02_PDUA_B | POLN02-DCSYS01a | POLN02 | POLN02 | 52.8 | 2.3 | 2024-04-04 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 454.1667 | EF13 RA | 5 | J&K 1 to 6 Amitie | 11.7 | EF10 Alcatel 7210 | 2 | EF10 Alcatel 7210 | 1.8 | E14 NOKIA 7750 SR12E(RA) | 1.3 | [21 empty] | 21.8 | 454.1667 | 0 | 0 | 279.8833 | 229.3833
POLN02_SEC_DD770_CD01 | POLN02-DCSYS01a | POLN02 | POLN02 | 140 | 40 | 2023-03-06 | 300 | 300 | 6 | 2 | 0 | 14 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 140 | 40
POLN02_SEC_DD770_EF01 | POLN02-DCSYS01a | POLN02 | POLN02 | 80 | 15 | 2023-03-06 | 300 | 300 | 6 | 1 | 2 | 24 | 11 | 0 | 31.25 | EF13 BT EAD | 0.5 | E11 Ciena 6500 R8 | 1 | [27 empty] | 1.5 | 31.25 | 0 | 0 | 95.625 | 30.625
RDG_SEC_DD770_FO | RDG;DC SYS01 | RDG | RDG | 125 | 125 | 2023-03-06 | 300 | 300 | 5 | 0 | 0 | 9 | 9 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 125 | 125
RDGCD1_SEC_CDDB_A05 | RDGCD1;DC SYS01 | RDGCD1 | RDGCD1 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
RDGCD2_SEC_CDDB_TU09 | RDGCD1;DC SYS01 | RDGCD2 | RDGCD2 | 50 | 50 | 2020-11-27 | 300 | 300 | 4 | 0 | 0 | 3 | 1 | 26 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 50 | 50
SLO_SEC_DD770_AB0 | SLO;DC SYS01 | SLO | SLO | 160 | 160 | 2023-05-22 | 300 | 300 | 5 | 1 | 0 | 2 | 9 | 0 | 62.5 | AB04 Alcatel 7210 | 2 | AB03 BT EAD | 1 | [27 empty] | 3 | 62.5 | 0 | 0 | 191.25 | 191.25
SLO_SEC_DD770_AB00 | SLO;DC SYS01 | SLO | SLO | 170 | 170 | 2023-05-22 | 300 | 300 | 4 | 0 | 0 | 4 | 6 | 0 | 10.4167 | N5 Nokia 1830 ILA | 0.5 | [29 empty] | 0.5 | 10.4167 | 0 | 0 | 175.2083 | 175.2083
WHHN03_SEC_DD770_CD01_01 | WHHN03;DC SYS01 | WHHN03 | WHHN03 | 80 | 90 | 2020-07-30 | 300 | 300 | 0 | 8 | 0 | 17 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 90
WHHN03_SEC_DD770_EF01_02 | WHHN03;DC SYS01 | WHHN03 | WHHN03 | 80 | 70 | 2020-07-30 | 0 | 0 | 5 | 10 | 0 | 6 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 70
WHHN03_SEC_Eaton CBDB_LM01 | WHHN03;DC SYS01 | WHHN03 | WHHN03 | 90 | 90 | 2017-09-05 | 300 | 300 | 1 | 0 | 2 | 1 | 0 | 12 | 20.8333 | NP11 Alcatel 7210 | 1 | [29 empty] | 1 | 20.8333 | 0 | 0 | 100.4167 | 100.4167
OHB_SEC_DCDB01_WALL_OPP TO SUITE EF | OHB;DC SYS02;PSU2 | OHB | OHB | N/A | N/A | 2023-03-13 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
OHB_SEC_DCDB03_WALL | OHB;DC SYS02;PSU2 | OHB | OHB | 0 | 50 | 2023-03-13 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 41.6667 | J04 Nokia 1830 | 2 | [29 empty] | 2 | 41.6667 | 0 | 0 | 20.8333 | 70.8333
OHB_SEC_DCDB04_WALL | OHB;DC SYS01;PSU1 | OHB | OHB | 45 | 0 | 2023-03-13 | 300 | 300 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 45 | 0
OHB_SEC_DCDB05_WALL | OHB;DC SYS02;PSU2 | OHB | OHB | 0 | 85 | 2023-03-13 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 85
OHB_SEC_DCDB06_WALL | OHB;DC SYS01;PSU1 | OHB | OHB | 80 | 7 | 2017-06-28 | 300 | 300 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 80 | 7
SWNN03_DCDB 1 | SWNN03;DC SYS01 | SWNN03 | SWNN03 | 61 | 93 | 2023-03-14 | 300 | 300 | 0 | 2 | 0 | 0 | 0 | 29 | 125 | JH01 RA | 5 | D5 BT EAD | 1 | [27 empty] | 6 | 125 | 0 | 0 | 123.5 | 155.5
SWNN03_SYS01_PER_K - ignore | SWNN03;DC SYS01 | SWNN03 | SWNN03 | 0 | 0 | 2009-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SQYN02_SEC_DCDB_HVHU1 | SQYN02;DC SYS07 | SQYN02 | SQYN02 | 63 | 59 | 2023-04-18 | 300 | 300 | 3 | 0 | 2 | 0 | 0 | 36 | 333.3333 | JQ4 Nokia 7750 SR-7B | 2.5 | JQ5 Nokia 7750 SR-7B | 2.5 | JS3 Nokia 7750 SR-2s | 11 | [25 empty] | 16 | 333.3333 | 0 | 0 | 229.6667 | 225.6667
LLDTE1_SEC_DCDB_Q4 | LLDTE1;DC SYS01 | LLDTE1 | LLDTE1 | 97 | 101 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 97 | 101
BSHN08_PDU2A_B | BSH;DC SYS02;GND | BSHN08 | BSHN08 | 110.4 | 114.4 | 2024-04-17 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3333 | HomeBB DNS B7 | 1.4 | A7 Netflix | 2.2 | Sky | 2 | A09 QWILT | 4 | A10 Nokia 7750SR7s | 2.3 | A6 IGW+Wsai | 1.7 | [19 empty] | 13.6 | 283.3333 | 0 | 0 | 252.0667 | 256.0667
BTLN09_PDU2A_B | BTLN09;DC SYS01 | BTLN09 | BTLN09 | 13 | 13 | 2024-04-18 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 418.75 | B24 Ciena6500 R8 | 1.7 | Nokia SEGW | 7.5 | B22 Waverserver_5 | 2 | B13 Nokia SEGGW ESA | 2.9 | A11 QWILT | 6 | [21 empty] | 20.1 | 418.75 | 0 | 0 | 222.375 | 222.375
LDSCD2_PDU2A_B | LDSCD2;DC SYS A | LDSCD2 | LDSCD2 | 10.5 | 11.1 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 291.6667 |  |  | XY 05 BT EAD | 1 | X6 QWILT | 3.4 | AB7 W5 | 3.6 | Nokia 7750 SR-7s AB13 | 6 | [21 empty] | 14 | 291.6667 | 0 | 0 | 156.3333 | 156.9333
MCRCD2_PDU2A_B | MCRCD2;DC SYS02 [Rect 3&4] | MCRCD2 | MCRCD2 | 11 | 15.1 | 2024-03-13 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 162.5 | T06 W5 | 3.6 | T07 RLS & Waveserver | 4.2 | [27 empty] | 7.8 | 162.5 | 0 | 0 | 92.25 | 96.35
SQYN02_PDU2A_B | SQYN02;DC SYS08A | SQYN02 | SQYN02 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
CHTTN3_PDU2A_B | CHTTN3;DC SYS01A | CHTTN3 | CHTTN3 | 0 | 0.3 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0.3
STGCD1_Eaton DIST@G0 | STGCD1;DC SYS01 | STGCD1 | STGCD1 | 0 | 0 | 2022-10-26 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
SHDTR1_SEC_CBDB_N10 | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 140 | 137 | 2023-02-14 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 114.5833 | M5a IGW, M5 IGW | 5.5 | [29 empty] | 5.5 | 114.5833 | 0 | 0 | 197.2917 | 194.2917
SHDTR1_EOS_D | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 3 | 2.7 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 3 | 2.7
SHDTR1_EOS_E | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | N/A | N/A | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | #VALUE! | #VALUE!
SHDTR1_EOS_F | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 2.5 | 2.5 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 2.5 | 2.5
SHDTR1_EOS_G | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 2.8 | 1.9 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 2.8 | 1.9
SHDTR1_EOS_H | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 13.2 | 10.8 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 13.2 | 10.8
SHDTR1_EOS_J | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 9.6 | 9.1 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 9.6 | 9.1
SHDTR1_EOS_K | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 30.4 | 31.4 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 30.4 | 31.4
SHDTR1_EOS_L | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 25.7 | 25.7 | 2023-02-14 | 80 | 80 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 25.7 | 25.7
SHDTR1_EOS_M | SHDTR1;DC SYS01 | SHDTR1 | SHDTR1 | 0 | 0 | 2023-02-14 | 80 | 80 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0
Note on R23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 3.2KW
Note on T23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8.5kW allocation reduced due to live reading of 3kW Reply: 8.5kW allocation reduced due to live reading of 4.05kW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.1KW Reply: 8.5kW allocation reduced due to live reading of 3.2KW
Note on V23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW Reply: 2kW allocation reduced due to live reading of 0.4KW
Note on X23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of .27KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.1KW Reply: 2kW allocation reduced due to live reading of 0.1KW Reply: 2kW allocation reduced due to live reading of 0.1KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW Reply: 2kW allocation reduced due to live reading of 0.2KW
Note on R30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8kw, live readings show running at 6.7kW currently Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7KW
Note on T30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.2KW
Note on V30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 2.5kW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 3KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.9KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 3.4KW Reply: 4kW allocation reduced due to live reading of 3.2KW Reply: 4kW allocation reduced due to live reading of 3KW Reply: 4kW allocation reduced due to live reading of 2.7KW
Note on X30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 16kW allocations reduced due to live reading of 4kW Reply: Live reading of 5kW allocated load remaining 11kW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5.1KW Reply: 6kW allocation reduced due to live reading of 5.1KW Reply: 16kW allocation reduced due to live reading of 5KW Reply: 16kW allocation reduced due to live reading of 5.3KW Reply: 16kW allocation reduced due to live reading of 5.5KW Reply: 16kW allocation reduced due to live reading of 5.1KW
Note on Z30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 7kW allocation reduced due to live reading of 1.5kW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 3.7KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 4.8KW Reply: 7kW allocation reduced due to live reading of 4.8KW Reply: 7kW allocation reduced due to live reading of 5.2KW
Note on AB30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3.7kW allocation reduced due to live reading of 1.5kW Reply: 3.7kW allocation reduced due to Live reading of 1.7kW Reply: 1kW added, taken from QWILT as now 10x server 4.25kW requirement Reply: 4.25kW allocation reduced due to live reading of 1.6KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.7KW Reply: 4.25kW allocation reduced due to live reading of 1.6KW
Note on AD30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Google rack new allocated load of 4.5kW. Live load 2kW remaining allocation 2.5kW Reply: 4.5kW allocation reduced due to live reading of 2.3KW
Note on AH30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW Reply: 3kW allocation reduced due to live reading of 0.6KW
Note on AJ30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.2KW Reply: 4kW allocation reduced due to live reading of 0.9KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 0.8KW Reply: 4kW allocation reduced due to live reading of 1.1KW
Note on AL30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 5kW to 3kW based on figures for other RA's Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW Reply: 5kW allocation reduced due to live reading of 2.5KW
Note on AN30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of .05 KW so original 4kW Reply: 4kW allocation reduced due to live reading of 0.1KW Reply: 4kW allocation reduced due to live reading of 0.1KW
Note on Q38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Ciena 6500-7(1.1KW) into existing cab AB2-ORMT_SAP_231122_3_26168659
Note on T44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 3KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 3KW Reply: 5kW allocation reduced due to live reading of 3.7KW
Note on V44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 4.5kW allocation reduced due to live reading of 1.6KW Reply: 4.5kW allocation reduced due to live reading of 1.6KW Reply: 4.5kW allocation reduced due to live reading of 1.6KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW Reply: 4.5kW allocation reduced due to live reading of 1.8KW Reply: 4.5kW allocation reduced due to live reading of 1.7KW
Note on X44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.9KW Reply: 4.5kW allocation reduced due to live reading of 2.9KW Reply: 4.5kW allocation reduced due to live reading of 3.1KW Reply: 4.5kW allocation reduced due to live reading of 3.1KW Reply: 4.5kW allocation reduced due to live reading of 3.1KW Reply: 4.5kW allocation reduced due to live reading of 3.1KW Reply: 4.5kW allocation reduced due to live reading of 3.1KW Reply: 4.5kW allocation reduced due to live reading of 3.2KW Reply: 4.5kW allocation reduced due to live reading of 3.6KW Reply: 4.5kW allocation reduced due to live reading of 3.6KW
Note on Z44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 1.5kW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 1.9KW Reply: 4.5kW allocation reduced due to live reading of 2.1KW Reply: 4.5kW allocation reduced due to live reading of 2.1KW
Note on AB44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.6KW Reply: 6.5kW allocation reduced due to live reading of 5.5KW Reply: 6.5kW allocation reduced due to live reading of 5.5KW Reply: 6.5kW allocation reduced due to live reading of 5.6KW Reply: 6.5kW allocation reduced due to live reading of 5.5KW Reply: 6.5kW allocation reduced due to live reading of 5.6KW Reply: 6.5kW allocation reduced due to live reading of 5.5KW Reply: 6.5kW allocation reduced due to live reading of 5.6KW Reply: 6.5kW allocation reduced due to live reading of 5.6KW Reply: 6.5kW allocation reduced due to live reading of 5.6KW
Note on W57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional BT EAD[KA7] 0.5 KW into existing cab C03-ORMT_SAP_231218_9_Y861526
Note on T68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Ciena 6500-14 slot with power upgrade in existing CAB F03- ORMT_SAP_230821_19_26168659
Note on S73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Utility Cab planned for ORMT_SAP_240301_3_Y857169
Note on R87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW
Note on T87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6.7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7kW
Note on V87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4 due to live reading of 700w Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 1kW
Note on X87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.6kW
Note on Z87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW
Note on AB87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live redaing of 4kW Reply: 6kW allocation reduced due to live reading of 4.5kW Reply: 6kW allocation reduced due to live reading of 4.4kW Reply: 6kW allocation reduced due to live reading of 4.5kW Reply: 6kW allocation reduced due to live reading of 4.4kW Reply: 6kW allocation reduced due to live reading of 4.6kW Reply: 6kW allocation reduced due to live reading of 4.7kW Reply: 6kW allocation reduced due to live reading of 4.7kW Reply: 6kW allocation reduced due to live reading of 4.7kW Reply: 6kW allocation reduced due to live reading of 5.1kW
Note on AD87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW
Note on AF87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5.4kW allocation reduced due to live reading of 1.4kW Reply: 5.4kW allocation reduced due to live reading of 1.4kW Reply: 5.4kW allocation reduced due to live reading of 1.4kW Reply: 5.4kW allocation reduced due to live reading of 1.4kW
Note on AH87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW
Note on S94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDU installation planned for ORMT_SAP_240424_8_11407175
Note on R116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.5kW
Note on T116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 13.5kW reduced due to live reading of 3.5kW Reply: 13.5kW allocation reduced due to live reading of 1.4kW Reply: 13.5kW allocation reduced due to live reading of 6.1kW Reply: 13.5kW allocation reduced due to live reading of 6.1kW Reply: 13.5kW allocation reduced due to live reading of 6.2kW Reply: 13.5kW allocation reduced due to live reading of 6.2kW Reply: 13.5kW allocation reduced due to live reading of 6.2kW Reply: 13.5kW allocation reduced due to live reading of 6.2kW Reply: 13.5kW allocation reduced due to live reading of 6.2kW Reply: 13.5kW allocation reduced due to live reading of 6.3kW
Note on V116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4.5kW allocation reduced due to live reading of 1kW Reply: 4.5kW allocation reduced due to live reading of 1.9kW
Note on X116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW
Note on Z116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 32.8A, so 4.5kW allocation reduced by 1.8kW Reply: 2.25kW allocation reduced due to live reading of 1kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 1.9kW Reply: 4.5kW allocation reduced due to live reading of 1.9kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2.2kW Reply: 4.5kW allocation reduced due to live reading of 2.4kW Reply: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW
Note on Q117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211015_16_11135118
Note on T117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocated, live so halved to 2.5kw
Note on V117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As per glen advise 2KW power is allocated for this live rack
Note on R143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 6.3kW, so original 8kW reduced Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.1kW
Note on T143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.3KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.3KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW Reply: 5kW allocation reduced due to live reading of 2.4KW
Note on V143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.1KW Reply: 2kW allocation reduced due to live reading of 0.1kW Reply: 2kW allocation reduced due to live reading of 0.1kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on X143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4.5kW allocation reduced due to live reading of 1.3KW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW
Note on Z143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 2.1KW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.1kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW
Note on AB143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 0.9KW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW
Note on AD143: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: John Womersley. provisional allocation for end of life load Reply: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW
Note on W148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade given for ORMT_SAP_240415_18_Y854576
Note on R156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.4kW Reply: 5kW allocation reduced due to live reading of 3.5kW Reply: 5kW allocation reduced due to live reading of 3.9kW Reply: 5kW allocation reduced due to live reading of 3.9kW
Note on T156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 1kW Reply: 5kW allocation reduced due to live reading of 0.1kW
Note on R170: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for virgin media NTE rack BH18- ORMT_SAP_240102_12_Y855684
Note on Q173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C02- ORMT_SAP_240425_5_10330814x
Note on S173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: additional 40 amps power upgrade for Cisco 6300 rack C04- ORMT_SAP_240425_5_10330814x
Note on R176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kw, live reading of 2.5kW so reduced down Reply: 5kW allocation reduced due to live reading of 2.8KW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.8kW
Note on T176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8Kw, live reading of 6kW, so reduced down Reply: 8kW allocation reduced due to live reading of 7.2KW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.4kW Reply: 8kW allocation reduced due to live reading of 7.3kW
Note on V176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1KW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW
Note on X176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 4kW allocation reduced due to live reading of 1.1KW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.3kW
Note on Z176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 4kW allocation reduced due to live reading of 1.4KW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW
Note on AB176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 700W Reply: 4kW allocation reduced due to live reading of 0.7KW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on AH176: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW Reply: 1kW allocation reduced due to live reading of 0.2KW
Note on R191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.7kW Reply: 5kW allocation reduced due to live reading of 2.7kW Reply: 5kW allocation reduced due to live reading of 2.7kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 3kW
Note on T191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6kW Reply: 8kW allocation reduced due to live reading of 6.8kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.4kW Reply: 8kW allocation reduced due to live reading of 7.5kW Reply: 8kW allocation reduced due to live reading of 7.5kW
Note on V191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 67A, so 16kW allocation reduced by 3.7kW Reply: 8kW allocation reduced due to live reading of 5.6kW Reply: 8kW allocation reduced due to live reading of 5.6kW Reply: 8kW allocation reduced due to live reading of 5.5kW Reply: 8kW allocation reduced due to live reading of 5.8kW Reply: 8kW allocation reduced due to live reading of 5.8kW Reply: 8kW allocation reduced due to live reading of 5.9kW Reply: 8kW allocation reduced due to live reading of 5.9kW Reply: 8kW allocation reduced due to live reading of 5.8kW Reply: 8kW allocation reduced due to live reading of 5.9kW Reply: 8kW allocation reduced due to live reading of 5.9kW
Note on V195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade planned under ORMT_SAP_231017_2_Y855640
Note on Q197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211015_16_11135118
Note on X197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for 10 servers, but 6 servers to be installed from Day1 ORMT_SAP_231011_14_10335416
Note on Z197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocation for additional 2 servers, to the existing 8,. 10 servers total for the rack ORMT_SAP_231011_14_10335416
Note on U200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Power upgrade given for ORMT_SAP_230607_9_Y854413
Note on R217: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.3kW Reply: 5kW allocation reduced due to live reading of 3.2kW
Note on T217: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.8kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW Reply: 12kW allocation reduced due to live reading of 1.7kW
Note on V217: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW
Note on Q219: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_230809_13_Y854576 - Given for power upgrade
Note on S236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DE4 utility rack is planned under ORMT_SAP_230907_9_Y850155
Note on R255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Readings taken 13/04, reduced from 8 to 6 Reply: 12kW allocation reduced due to live reading of 5.5kW Reply: 12kW allocation reduced due to live reading of 5.7kW Reply: 12kW allocation reduced due to live reading of 5.7kW Reply: 12kW allocation reduced due to live reading of 6kW Reply: 12kW allocation reduced due to live reading of 6kW Reply: 12kW allocation reduced due to live reading of 6.4kW Reply: 12kW allocation reduced due to live reading of 6.3kW Reply: 12kW allocation reduced due to live reading of 6.9kW Reply: 12kW allocation reduced due to live reading of 7kW
Note on T255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW total but confirmed currently running at 3.5kW, so 0.75kw left per system Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.2kW Reply: 5kW allocation reduced due to live reading of 3.2kW Reply: 5kW allocation reduced due to live reading of 3.6kW
Note on X255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6.5kW reduced due to 5.6kW live reading Reply: 6.5kW allocation reduced due to live reading of 5.7kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.7kW Reply: 6.5kW allocation reduced due to live reading of 5.7kW Reply: 6.5kW allocation reduced due to live reading of 5.7kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.7kW Reply: 6.5kW allocation reduced due to live reading of 5.7kW
Note on Z255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on AB255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on AD255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on R265: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_231109_20_10335416
Note on R266: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_231109_20_10335416
Note on R267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 6kW allocation reduced due to onsite reading of 3.9kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.8kW Reply: 6kW allocation reduced due to live reading of 4.8kW
Note on T267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.7kW Reply: 4.5kW allocation reduced due to live reading of 2.9kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.9kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.9kW
Note on V267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.9kW allocation reduced due to live reading of 1.1kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW Reply: 2.9kW allocation reduced due to live reading of 1.2kW
Note on X267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Totla 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2.9kW Reply: 4.5kW allocation reduced due to live reading of 2.7kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 3.4kW Reply: 4.5kW allocation reduced due to live reading of 2.7kW Reply: 4.5kW allocation reduced due to live reading of 2.9kW
Note on Z267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.8kW allocation reduced due to live reading of 1kW Reply: 1.8kW allocation reduced due to live reading of 0.9kW Reply: 1.8kW allocation reduced due to live reading of 1kW Reply: 1.8kW allocation reduced due to live reading of 1kW Reply: 1.8kW allocation reduced due to live reading of 1kW Reply: 1.8kW allocation reduced due to live reading of .9kW Reply: 1.8kW allocation reduced due to live reading of 1kW Reply: 1.8kW allocation reduced due to live reading of 0.9kW Reply: 1.8kW allocation reduced due to live reading of 0.9kW
Note on AB267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total 4kW allocation reduced due to live reading of 2.2kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW
Note on AD267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.5kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW
Note on AF267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW
Note on AH267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW
Note on AJ267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.7kW Reply: 4.5kW allocation reduced due to live reading of 2.7kW Reply: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.6kW Reply: 4.5kW allocation reduced due to live reading of 2.8kW Reply: 4.5kW allocation reduced due to live reading of 2.7KW Reply: 4.5kW allocation reduced due to live reading of 2.8KW
Note on AL267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5.5kW allocation reduced due to live reading of 1.3kW Reply: 5.5kW allocation reduced due to live reading of 1.3kW
Note on R268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3.2kW
Note on V268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4KW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW
Note on X268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kw allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 2kW Reply: 4kW allocation reduced due to live reading of 2kW
Note on Z268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4kW by 600W from live on site reading Reply: Live reading of 1.47 KW so original 4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.8kW
Note on AB268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW
Note on AD268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW Reply: 4kW allocation reduced due to live reading of 1.7kW
Note on R275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 116A, so original 8kW reduced down
Note on T275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 44.5A so original 4kW reduced down Reply: 5kW allocation reduced due to live reading of 3KW Reply: 5KW allocation reduced due to live reading of 3KW Reply: 5KW allocation reduced due to live reading of 3KW Reply: 5KW allocation reduced due to live reading of 3.1KW Reply: 5KW allocation reduced due to live reading of 3.1KW Reply: 5KW allocation reduced due to live reading of 3KW Reply: 5KW allocation reduced due to live reading of 3.1KW Reply: 5KW allocation reduced due to live reading of 3.4KW Reply: 5KW allocation reduced due to live reading of 3.4KW Reply: 5KW allocation reduced due to live reading of 3.4KW
Note on V275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 12.2A so original 4.5kW reduced down Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.2kW Reply: 4.5kW allocation reduced due to live reading of 1.2kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.2kW Reply: 4.5kW allocation reduced due to live reading of 1.3kW Reply: 4.5kW allocation reduced due to live reading of 1.7kW Reply: 4.5kW allocation reduced due to live reading of 1.6kW Reply: 4.5kW allocation reduced due to live reading of 1.7kW Reply: 4.5kW allocation reduced due to live reading of 1.7kW
Note on X275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 11.8A so original 4.5kW reduced down Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2.1kW Reply: 4.5kW allocation reduced due to live reading of 2kW Reply: 4.5kW allocation reduced due to live reading of 2.4kW Reply: 4.5kW allocation reduced due to live reading of 2.4kW Reply: 4.5kW allocation reduced due to live reading of 2.4kW Reply: 4.5kW allocation reduced due to live reading of 2.4kW
Note on Z275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 6.3A so original 4.5kW reduced down Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of 0.9kW Reply: 4.5kW allocation reduced due to live reading of1kW Reply: 4.5kW allocation reduced due to live reading of1kW Reply: 4.5kW allocation reduced due to live reading of1kW Reply: 4.5kW allocation reduced due to live reading of1kW
Note on AB275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.3KW Reply: 5kW allocation reduced due to live reading of 0.3KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.5KW
Note on AD275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.9kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on AF275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 7.1KW Reply: 8kW allocation reduced due to live reading of 7.2KW Reply: 8kW allocation reduced due to live reading of 7.2KW Reply: 8kW allocation reduced due to live reading of 7.2KW Reply: 8kW allocation reduced due to live reading of 7.2KW Reply: 8kW allocation reduced due to live reading of 7.3KW Reply: 8kW allocation reduced due to live reading of 7.3KW Reply: 8kW allocation reduced due to live reading of 7.3KW
Note on U285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ciena 6500 14slot and Alcatel 7210 SAS SX Planned - ORMT_SAP_231025_22_Y858601
Note on W285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on Y285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on S287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on U287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver planned- CPL Removal project
Note on W287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IGW(3.5KW) into L06-ORMT_SAP_231011_4_10335416
Note on S290: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211216_4_w122836 - CPL - 3 x Ciena 6500-14 (@2kW each) - in existing racks - Positions G1, H1 & E1
Note on Y299: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Marconi MSPP 1684 is planned under ORMT_SAP_231103_12_y842157
Note on R302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 9th Aug - reduced to 1.5kW as now on (using figures for other nodes) Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3.1kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 2kW Reply: 5kW allocation reduced due to live reading of 3kW
Note on T302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 9th Aug reduced to 2.5kw as turn on (using figures from other live sites) originally 8kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.8kW Reply: 8kW allocation reduced due to live reading of 6.9kW Reply: 8kW allocation reduced due to live reading of 6.9kW Reply: 8kW allocation reduced due to live reading of 6.9kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 7kW Reply: 8kW allocation reduced due to live reading of 6.9kW Reply: 8kW allocation reduced due to live reading of 6.9kW
Note on V302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.5kW Reply: 4kW allocation reduced due to live reading of 1.4kW Reply: 4kW allocation reduced due to live reading of 1.5kW
Note on X302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on Z302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW Reply: 1kW allocation reduced due to live reading of 0.4kW
Note on AB302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.4kW Reply: 4kW allocation reduced due to live reading of 0.4kW Reply: 4kW allocation reduced due to live reading of 0.4kW Reply: 4kW allocation reduced due to live reading of 0.4kW Reply: 4kW allocation reduced due to live reading of 0.4kW Reply: 4kW allocation reduced due to live reading of 0.4kW
Note on AD302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.5kW
Note on AL302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 0.6kW Reply: 2.5kW allocation reduced due to live reading of 0.6kW
Note on AN302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_220915_12_31256
Note on AP302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_220915_12_31256
Note on AR302: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_220915_12_31256
Note on R310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocated, currently 6kW live
Note on T310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.3kW Reply: 4kW allocation reduced due to live reading of 1.5kW
Note on V310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on X310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.8kW Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 2.9kW
Note on Z310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.5kW
Note on AB310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.5kW
Note on AD310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.5kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.6kW Reply: 8kW allocation reduced due to live reading of 6.8kW
Note on AF310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on AG310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver rack is planned under CPL removal project.
Note on AH310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.9kW
Note on AI310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: WAVESERVER 5 Rack is planned- ORMT_SAP_231110_8_w014433
Note on AJ310: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.4kW
Note on R320: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated 2kW reduction as box now in service. Reduced from 5kW to 3kW
Note on R333: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: reduced from 5kW to 3kW estimated
Note on R339: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional XG210 is planned in existing rack E10 under ORMT_SAP_240212_3_w019357
Note on R359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 2.9KW Reply: 5kW allocation reduced due to live reading of 3.2KW Reply: 5kW allocation reduced due to live reading of 3.2KW
Note on T359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed running at 6kW at the moment Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.9KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW Reply: 8kW allocation reduced due to live reading of 6.8KW
Note on V359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated actual load readings from AxScada; 3.4kW used; 10.3kW remaining Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5KW Reply: 14kW allocation reduced due to live reading of 5.1KW Reply: 14kW allocation reduced due to live reading of 5.1KW Reply: 11kW allocation reduced due to live reading of 5.1KW Reply: 11kW allocation reduced due to live reading of 5.4KW Reply: 11kW allocation reduced due to live reading of 5.6KW Reply: 11kW allocation reduced due to live reading of 6.2KW Reply: 11kW allocation reduced due to live reading of 6.3KW
Note on X359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4kW due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.4KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.5KW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.6KW Reply: 4kW allocation reduced due to live reading of 2.7KW Reply: 4kW allocation reduced due to live reading of 2.8KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.1KW
Note on Z359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 4kW due to live reading of 2.3kW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 1.9KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.3KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW Reply: 4kW allocation reduced due to live reading of 2.2KW
Note on AB359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.1KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW Reply: 12kW allocation reduced due to live reading of 0.3KW
Note on AD359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 7kW after live readings of 3.5kW Reply: 7kW allocation reduced due to live reading of 4KW Reply: 7kW allocation reduced due to live reading of 4.1KW Reply: 7kW allocation reduced due to live reading of 4.1KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.5KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.6KW Reply: 7kW allocation reduced due to live reading of 4.7KW Reply: 7kW allocation reduced due to live reading of 5.1KW
Note on AF359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 3.7kW due to live reading of 1.1kW Reply: 3.7kW allocation reduced due to live reading of 1.3KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.6KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.5KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW Reply: 3.7kW allocation reduced due to live reading of 1.5KW Reply: 3.7kW allocation reduced due to live reading of 1.6KW Reply: 3.7kW allocation reduced due to live reading of 1.4KW
Note on AH359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced from 2.6kW due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.2KW Reply: 2.6kW allocation reduced due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.4kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.2kW Reply: 2.6kW allocation reduced due to live reading of 1.3kW Reply: 2.6kW allocation reduced due to live reading of 1.3kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.5kW Reply: 2.6kW allocation reduced due to live reading of 1.4kW
Note on AL359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW Reply: 1kW allocation reduced due to live reading of 0.1KW
Note on R365: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 7kW allocation reduced due to live reading of 0.8kW
Note on R369: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on R372: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on R377: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on R378: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.2kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on R381: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW
Note on T381: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12 kW allocation reduced due to live reading of 0.1 kW Reply: 12 kW allocation reduced due to live reading of 0.1 kW Reply: 12 kW allocation reduced due to live reading of 0.1 kW Reply: 12 kW allocation reduced due to live reading of 0.1 kW Reply: 12 kW allocation reduced due to live reading of 0.1 kW Reply: 12 kW allocation reduced due to live reading of 0.1 kW
Note on R383: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2.5kW allocation reduced due to live reading of 1.1kW Reply: 5kW allocation reduced due to live reading of 1.1kW Reply: 5kW allocation reduced due to live reading of 1.1kW Reply: 5kW allocation reduced due to live reading of 0.2kW Reply: 5kW allocation reduced due to live reading of 0.5kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.5kW Reply: 5kW allocation reduced due to live reading of 0.4kW
Note on T383: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 3.8kW Reply: 12kW allocation reduced due to live reading of 3.9kW Reply: Allocated load corrected back to 12kW as the 3.9kW reading is due to spurious load on AxScada Reply: 12kW allocation reduced due to live reading of 0.1kW
Note on V383: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.1kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.2kW
Note on R393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 5kW but confirmed currently running at 3.5kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 4kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW Reply: 5kW allocation reduced due to live reading of 2.6kW
Note on T393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jul-21 Was 8kW, confirmed currently running at 6kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.1kW Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW
Note on V393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 1.9kW
Note on X393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 800w Reply: 4kW allocation reduced due to live reading of 1.9kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 01.3kW
Note on Z393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW
Note on AB393: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.7kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.8kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW Reply: 4.2kW allocation reduced due to live reading of 0.9kW
Note on Q397: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ORMT_SAP_211015_16_11135118
Note on R405: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.1kW Reply: 6kW allocation reduced due to live reading of 0.2kW Reply: 6kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on T405: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.6kW Reply: 4kW allocation reduced due to live reading of 0.5kW Reply: 4kW allocation reduced due to live reading of 0.6kW
Note on R412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.7kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.7kW Reply: 5kW allocation reduced due to live reading of 0.7kW Reply: 5kW allocation reduced due to live reading of 0.7kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.7kW Reply: 5kW allocation reduced due to live reading of 0.7kW
Note on T412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.2kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW Reply: 5kW allocation reduced due to live reading of 0.3kW
Note on V412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.3kW Reply: 5kW allocation reduced due to live reading of 2.3kW Reply: 5kW allocation reduced due to live reading of 2.3kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 2.4kW
Note on X412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW Reply: 2kW allocation reduced due to live reading of 0.4kW
Note on Z412: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.2kW Reply: 1kW allocation reduced due to live reading of 0.3kW
Note on R425: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allocated under ORMT_SAP_231109_20_10335416
Note on Q431: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDU installation planned for ORMT_SAP_240424_8_11407175
Note on Q433: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New AKAMAI rack is planned in BE09 under ORMT_SAP_231220_15_10335416
Note on T439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 101A, so 6.5kW allocation reduced by 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW Reply: 6.5kW allocation reduced due to live reading of 5.6kW Reply: 6.5kW allocation reduced due to live reading of 5.5kW
Note on V439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 50A, so 4kW allocation reduced by 2.7kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3.3kW
Note on X439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 43.5A, so 4kW allocation reduced by 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 2.4kW Reply: 4kW allocation reduced due to live reading of 3kW Reply: 4kW allocation reduced due to live reading of 3kW
Note on Z439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 20A, so 4kW allocation reduced by 1.1kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 2.7kW Reply: 4kW allocation reduced due to live reading of 3.1kW Reply: 4kW allocation reduced due to live reading of 3.1kW
Note on AB439: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 14kW Reply: 67kW allocation reduced due to live reading of 13.4kW Reply: 67kW allocation reduced due to live reading of 13.5kW
Note on R440: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 5kW, live reading of 2.5kW so reduced Reply: 5kW allocation reduced due to live reading of 2.9kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW Reply: 5kW allocation reduced due to live reading of 3kW
Note on T440: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 8kW, live reading of 6kW so reduced. Reply: 8kW allocation reduced due to live reading of 7.2kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.3kW Reply: 8kW allocation reduced due to live reading of 7.2kW
Note on V440: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.6kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 1.2kW Reply: 4kW allocation reduced due to live reading of 2.1kW
Note on R441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 38kW allocation reduced due to live reading of 3.4kW Reply: 38kW allocation reduced due to live reading of 1.7kW Reply: 38kW allocation reduced due to live reading of 1.7kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 3.9kW Reply: 38kW allocation reduced due to live reading of 1.8kW Reply: 38kW allocation reduced due to live reading of 1.8kW
Note on T441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 60A, so 6kW allocation reduced by 3.2kW Reply: 6kW allocation reduced due to live reading of 3.3kW Reply: 6kW allocation reduced due to live reading of 3.4kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.6kW
Note on X441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on Z441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading 64A, so 4.75kW allocation reduced by 3.5kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW Reply: 4.75kW allocation reduced due to live reading of 4.3kW
Note on AB441: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 14.2kW allocation reduced due to live reading of 2kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW Reply: 14.2kW allocation reduced due to live reading of 2.1kW
Note on Q442: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This rack is planned for Alcatel 1626 & Ciena 6500- 7 slot installation under ORMT_SAP_240110_7_26168659[DCTN03 site closure]
Note on T447: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.1kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW Reply: 12kW allocation reduced due to live reading of 0.3kW
Note on X447: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW Reply: 2kW allocation reduced due to live reading of 0.2kW
Note on Z447: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Live reading of 2.23 KW so original 5 kW Reply: Live reading of 2.5 KW so original 5 kW Reply: 5kW allocation reduced due to live reading of 2.4kW Reply: 5kW allocation reduced due to live reading of 3.7kW Reply: 5kW allocation reduced due to live reading of 3.7kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 2.5kW Reply: 5kW allocation reduced due to live reading of 3.7kW
Note on U465: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Nokia 7750 SR-2s,Nokia 7210 SAS-S 110GE is planned in an existing cab JS3 under ORMT_SAP_231012_19_26168659
Note on R467: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will be on new iPDUs due Jan 2022 Reply: 2kW allocation reduced due to live reading of 0.5KW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 5kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on T467: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 1.8KW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW Reply: 4kW allocation reduced due to live reading of 1.8kW
Note on X467: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: planned for ORMT_SAP_220607_5_10335416
Note on Z467: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 8kW allocation reduced due to live reading of 5.7KW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 4kW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 5.7kW Reply: 8kW allocation reduced due to live reading of 5.7kW
Note on AB467: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6kW allocation reduced due to live reading of 3.9KW Reply: 6kW allocation reduced due to live reading of 3.9kW Reply: 6kW allocation reduced due to live reading of 4kW Reply: 6kW allocation reduced due to live reading of 4.1kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.2kW Reply: 6kW allocation reduced due to live reading of 4.3kW Reply: 6kW allocation reduced due to live reading of 4.3kW
Note on R468: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW
Note on U468: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Waveserver_5(2.0KW)into B22-ORMT_SAP_231123_10_w014433
Note on X468: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ESA400s @ 520W each only 2 planned day 1 Reply: 4kW allocation reduced due to live reading of 0.7kW Reply: 4kW allocation reduced due to live reading of 0.8kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW Reply: 4kW allocation reduced due to live reading of 1.1kW
Note on Z468: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 6.5kW allocation reduced due to live reading of 0.5kW Reply: 6.5kW allocation reduced due to live reading of 0.5kW
Note on V469: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4kW allocation reduced due to live reading of 0.2kW Reply: 4kW allocation reduced due to live reading of 0.3kW Reply: 4kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.3kW Reply: 2kW allocation reduced due to live reading of 0.6kW
Note on X469: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.2kW Reply: 4.2kW allocation reduced due to live reading of 0.3kW Reply: 4.2kW allocation reduced due to live reading of 0.3kW Reply: 4.2kW allocation reduced due to live reading of 0.3kW Reply: 4.2kW allocation reduced due to live reading of 0.3kW Reply: 4.2kW allocation reduced due to live reading of 0.3kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW
Note on R470: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.4kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW Reply: 4.2kW allocation reduced due to live reading of 0.6kW
Note on S470: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: RLS & Waveserver rack is planned- CPL removal project.
Note on T470: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 5kW allocation reduced due to live reading of 0.2kW Reply: 5kW allocation reduced due to live reading of 0.8kW

## Site check - Dual
Dual DC Power System Capacity and Autonomy Checker
Site Select : | LDMS13 | Select which site with dual systems you need to check
Site Load : | 129 | Site total (A+B loads)
Site Load : | 7.0305 | Auto calculated
Allocated load : | 0 | Allocated load from Crown (A+B system)
Allocated load : | 0 | as above
Future Load: | 18 | Enter power requirements in Amps for future required (leave blank if not required)
| Power System A |  |  | Power System B
System names : | LDMS13;DC SYS01 A |  |  | LDMS13;DC SYS01 B
Load reading : | 45 |  |  | 84
Allocated load : | 0 | Allocated load in Crown |  | 0
Rect Type : | Eaton Powerware NPR.48 |  |  | Eaton Powerware NPR.48
Qty of Rect Fitted : | 8 |  |  | 8 | Cells will highlight red if different between systems
Existing Load in Amps : | 64.5 | Auto calculated |  | 64.5
New System Load Amps (Inc Future & New Loads) : | 73.5 | Auto calculated |  | 73.5
System Load : | 4.0057 | Auto calculated |  | 4.0057
Battery Strings Fitted : | 6 | Enter number of battery strings fitted to the system |  | 6
Battery Type : | 12V101F | Select battery type from drop down list |  | 12V101F | Cells will highlight red if different between systems
Battery Recharge Required : | 60 | Auto calculated (if cell is RED additional rectifier recharge is required) |  | 60
Required Load (Amps) : | 73.5 | Auto calculated |  | 73.5
| Available Rectifier Load Capacity | Additional Rect Required |  | Available Rectifier Load Capacity
Amps : | 192.5 | 5 |  | 192.5
kW : | 10.4913 |  |  | 10.4913
| A System Capacity Remaining | Combined System Capacity Remaining |  | B System Capacity Remaining
Percentage : | 61.82% | 90% Capacity limit exceeded if cells are red, additional build required |  | 61.82%
Amps : | 119 | 238 |  | 119
kW : | 6.4855 | 12.971 |  | 6.4855
Allowing for 10% for aging (Falcon) - Normal Running
Time (Hours) : | 1 hr | 2 hrs | 3 hrs | 4 hrs
System A Amps : | 301.5281 | 169.0745 | 123.4172 | 98.6862
System A kW : | 16.4333 | 9.2146 | 6.7262 | 5.3784
System B Amps : | 301.5281 | 169.0745 | 123.4172 | 98.6862
System B kW : | 16.4333 | 9.2146 | 6.7262 | 5.3784
Allowing for 10% for aging (Falcon) - Fail Over Only Minimum 2 Hours Autonomy
Time (Hours) : | 1 hr | 2 hrs | 3 hrs | 4 hrs
System A Amps : | 301.5281 | 169.0745 | 123.4172 | 98.6862
System A kW : | 16.4333 | 9.2146 | 6.7262 | 5.3784
System B Amps : | 301.5281 | 169.0745 | 123.4172 | 98.6862
System B kW : | 16.4333 | 9.2146 | 6.7262 | 5.3784
Note on C36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 10% as that is what PNI calculations will use

## All
One year ago (for DC readings) | 2024-02-27
Sys with reading over 1 year old | 122
BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI | BOXI
General | General | General | General | General | Power | Power | Power | Power | Power | Power | Power | Power | Power | Power | Autonomy | Autonomy | Autonomy | Autonomy | Autonomy | Cooling | Cooling | Cooling | Cooling | Space | Space | Power | Power | Power | Power | Power | Autonomy | Autonomy | Cooling | Cooling | Cooling | Cooling | Cooling | Cooling
System Name | Region | City | Equipment Area Function | Equipment Area Code | Manufacturer | Module Size Amps | Installed Modules | Actual Load Amps | Actual Load kW | Reading Date | Max Agreed DC Ouput at 80% of N kW | Available DC Output @ 80% of N kW | Max DC Output Inc. Full Batt Recharge kW | Available DC Output inc. Full Batt Recharge kW | 48V Strings | Maker | Model | Battery Autonomy kW | Autonomy Remaining kW | AHU Num Installed | AHU Sensible Cooling | Agreed Operational Cooling Limit | Cooling Remaining kW | Available Suite Sections | Limit To Growth | Total Allocated Load kW | kW Load Remaining after total allocated (80% of N) | kW Load Remaining after total allocated (inc Full Batt recharge) | % Load Remaining after total allocated (80% of N) | % Load Remaining after total allocated (inc Full Batt recharge) | Remaining Autonomy (after allocated load) | % Autonomy Remaining | Total Agreed Operational Cooling Limit | Total Site Load kW | Total Cooling Remaining | Total Allocated Load kW | Remaining Cooling (after allocated load) | % Cooling Remaining | Capped | Dual/Single | Battery bracket removal | P-Core | RA | PX | Amitie | Op-EX | Battery bracket remove
ABH;DC SYS01 | ANGLIA | ALDEBURGH | Redstream Optical Network Site | ABH | Eaton Powerware APR48-ES | 36.6 | 5 | 34 | 1.853 | 2024-05-02 | 6.383 | 4.53 | 1.6219 | -0.23108 | 3 | Yuasa | EN480-2 | 13.1544 | 11.3014 | 2 | 10 | 7.5 | 5.647 | 23 |  | 0 | 4.53 | -0.23108 | 70.9699 | -14.2473 | 11.3014 | 85.9135 | 7.5 | 1.853 | 5.647 | 0 | 5.647 | 75.2933 |  | Single | EN480-2 | 0 | 0 | 0 | 0 | 0 | EN480-2
ABN;DC SYS01 | SCOTLAND | ABERDEEN | Redstream Optical Network Site | ABN | Duvine DD686 | 75 | 6 | 206 | 11.227 | 2022-01-13 11:00 | 16.35 | 5.123 | 3.7605 | -7.4665 | 3 | PowerSafe | DDm85-25 | 26.1144 | 14.8874 | 3 | 30 | 22.5 | 11.273 | 3 |  | 6.5 | -1.377 | -13.9665 | -8.422 | -371.4001 | 8.3874 | 32.1179 | 22.5 | 11.227 | 11.273 | 6.5 | 4.773 | 21.2133 |  | Single | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
ABNTB1;DC SYS01 | SCOTLAND | ABERDEEN | Redstream Optical Network Site | ABNTB1 | Eaton Powerware APR48 | 31 | 29 | 377 | 20.5465 | 2024-05-02 | 37.8448 | 17.2983 | 27.686 | 7.1395 | 3 | PowerSafe | DDm100-25 | 31.6872 | 11.1407 | 4 | 45 | 33.75 | 13.2035 | 13 |  | 2 | 15.2983 | 5.1395 | 40.4238 | 18.5635 | 9.1407 | 28.8467 | 33.75 | 20.5465 | 13.2035 | 2 | 11.2035 | 33.1956 |  | Single | DDm100-25 | 0 | 0 | 0 | 0 | 0 | DDm100-25
ABNTD1;DCSYS01 | SCOTLAND | ABERDEEN | Redstream Optical Network Site | ABNTD1 | Eaton Powerware APR48-ES | 36.6 | 15 | 177 | 9.6465 | 2024-05-02 | 22.3406 | 12.6941 | 13.7558 | 4.1093 | 2 | PowerSafe | DDm100-27 | 22.8528 | 13.2063 | 3 | 60 | 45 | 35.3535 | 0 |  | 5 | 7.6941 | -0.8907 | 34.4401 | -6.4751 | 8.2063 | 35.9094 | 45 | 9.6465 | 35.3535 | 5 | 30.3535 | 67.4522 |  | Single | DDm100-27 | 0 | 0 | 0 | 0 | 0 | DDm100-27
ACTN01;DC SYS01a | LONDON | LONDON | Redstream Optical Network Site | ACTN01 | Eaton Powerware APR48-ES | 36.6 | 60 | 739 | 40.2755 | 2024-05-02 | 94.1498 | 53.8743 | 63.1873 | 22.9118 | 5 | PowerSafe | DDm125-33 | 88.884 | 48.6085 | 11 | 747 | 560.25 | 519.9745 | 178 |  | 6.85 | 47.0243 | 16.0618 | 49.9463 | 25.4193 | 41.7585 | 46.9809 | 560.25 | 83.4395 | 476.8105 | 12.4 | 464.4105 | 82.8934 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | OPEX | DDm125-33
ACTN01;DC SYS01b | LONDON | LONDON | Redstream Optical Network Site | ACTN01 | Eaton Powerware APR48-ES | 36.6 | 60 | 792 | 43.164 | 2024-05-02 | 94.1498 | 50.9858 | 63.1873 | 20.0233 | 5 | PowerSafe | DDm125-33 | 88.884 | 45.72 | 11 | 747 | 560.25 | 517.086 | 178 |  | 5.55 | 45.4358 | 14.4733 | 48.2591 | 22.9054 | 40.17 | 45.1937 | [7 empty] | Single | DDm125-33 | [5 empty] | DDm125-33
ANSTW1; DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | ALNESS | Redstream Optical Network Site | ANSTW1 | Power One PMP 10.48 SIC | 22 | 4 | 12.9 | 0.70305 | 2021-10-14 12:10 | 2.8776 | 2.1745 | 3.4335 | 2.7304 | 3 | Enersys | SBS C11F | 2.592 | 1.8889 | 2 | 6.7 | 5.025 | 4.322 | 5 |  | 0.4 | 1.7746 | 2.3304 | 61.6677 | 67.8739 | 1.4889 | 57.4441 | 5.025 | 0.70305 | 4.322 | 0.4 | 3.922 | 78.0488 |  | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
ASH;DC SYS01 | SOUTH EAST | ASHFORD | Redstream Optical Network Site | ASH | Eaton Powerware APR48-ES | 36.6 | 12 | 151 | 8.2295 | 2022-05-10 12:00 | 17.5534 | 9.3239 | 15.6142 | 7.3847 | 9 | Enersys | 12V155F | 12.636 | 4.4065 | 2 | 13 | 9.75 | 1.5205 | 13 |  | 0.5 | 8.8239 | 6.8847 | 50.2688 | 44.0927 | 3.9065 | 30.9156 | 9.75 | 8.2295 | 1.5205 | 0.5 | 1.0205 | 10.4667 |  | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
ASMN02;DC SYS01 | THAMES VALLEY | AMERSHAM | Redstream Optical Network Site | ASMN02 | Duvine DD686 | 75 | 6 | 100 | 5.45 | 2022-01-18 15:00 | 16.35 | 10.9 | 13.952 | 8.502 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 4.6588 | 5 | 150 | 112.5 | 107.05 | 23 |  | 0 | 10.9 | 8.502 | 66.6667 | 60.9375 | 4.6588 | 46.0866 | 112.5 | 5.45 | 107.05 | 0 | 107.05 | 95.1556 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
AYRN01; DC SYS01 | SCOTLAND | AYR | GIS Migrated | AYRN01 | Power One PMP 11.48 | 23 | 5 | 10 | 0.545 | 2013-11-07 | 4.0112 | 3.4662 | 4.796 | 4.251 | 4 | Enersys | SBS C11F | 3.456 | 2.911 | 3 | 20 | 15 | 14.455 | 12 |  | 0 | 3.4662 | 4.251 | 86.413 | 88.6364 | 2.911 | 84.2303 | 15 | 0.545 | 14.455 | 0 | 14.455 | 96.3667 |  | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
AZTCD1&2;DC SYS01 | SOUTH WEST | BRISTOL | Redstream Optical Network Site | AZTCD1 | Eaton Powerware APR48-ES | 36.6 | 60 | 859 | 46.8155 | 2023-02-15 | 94.1498 | 47.3343 | 52.2873 | 5.4718 | 6 | PowerSafe | DDm125-33 | 106.6608 | 59.8453 | 3 | 65 | 75 | 28.1845 | 29 |  | 6.9 | 40.4343 | -1.4282 | 42.9468 | -2.7314 | 52.9453 | 49.6389 | 116.25 | 46.8155 | 69.4345 | 6.9 | 62.5345 | 53.7931 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
BCT;DC SYS01 | MIDLANDS | WEDNESBURY | Redstream Optical Network Site | BCT | Eaton Powerware APR48-ES | 36.6 | 9 | 106 | 5.777 | 2024-05-02 | 12.7661 | 6.9891 | 6.2294 | 0.45235 | 3 | PowerSafe | 2DDm85-15 | 15.1632 | 9.3862 | 7 | 36 | 27 | 21.223 | 19 |  | 2 | 4.9891 | -1.5476 | 39.0808 | -24.8445 | 7.3862 | 48.7114 | 27 | 5.777 | 21.223 | 2 | 19.223 | 71.1963 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
BDEN02;DC SYS01 | SOUTH WEST | BUDE | Redstream Optical Network Site | BDEN02 | Eaton Powerware NPR.48 | 55 | 5 | 111 | 6.0495 | 2023-03-02 | 9.592 | 3.5425 | 5.6331 | -0.41638 | 3 | Yuasa | EN480-2 | 13.1544 | 7.1049 | 2 | 30 | 22.5 | 16.4505 | 12 |  | 0 | 3.5425 | -0.41638 | 36.9318 | -7.3916 | 7.1049 | 54.0116 | 22.5 | 6.0495 | 16.4505 | 0 | 16.4505 | 73.1133 |  | Single | EN480-2 | 0 | 0 | 0 | 0 | 0 | EN480-2
BDEN06;DC SYS01 | SOUTH WEST | BUDE | Redstream Optical Network Site | BDEN06 | Duvine DD686 | 75 | 13 | 500 | 27.25 | 2023-05-02 | 39.24 | 11.99 | 35.4631 | 8.2132 | 3 | FIAMM | 2SLA1000 | 27.7992 | 0.5492 | 3 | 114.42 | 85.815 | 58.565 | 31 |  | 5.5 | 6.49 | 2.7132 | 16.5392 | 7.6506 | -4.9508 | -17.8091 | 85.815 | 27.25 | 58.565 | 5.5 | 53.065 | 61.8365 |  | Single | 2SLA1000 | 0 | 0 | 0 | 0 | 0 | 2SLA1000
BDFN02;DC SYS01a | NORTHERN HOME COUNTIES | BEDFORD | GIS Migrated - Capped | BDFN02 | Eaton Powerware APR48-ES | 36.6 | 74 | 862 | 46.979 | 2024-05-02 | 116.4905 | 69.5115 | 80.2131 | 33.2341 | 6 | PowerSafe | DDm125-33 | 106.6608 | 59.6818 | 6 | 215 | 161.25 | 114.271 | 38 | Power | 12.55 | 56.9615 | 20.6841 | 48.898 | 25.7864 | 47.1318 | 44.1885 | 161.25 | 110.853 | 50.397 | 24.2 | 26.197 | 16.2462 | Capped | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
BDFN02;DC SYS01b | NORTHERN HOME COUNTIES | BEDFORD | GIS Migrated - Capped | BDFN02 | Eaton Powerware APR48-ES | 36.6 | 74 | 1172 | 63.874 | 2024-05-02 | 116.4905 | 52.6165 | 80.2131 | 16.3391 | 6 | PowerSafe | DDm125-33 | 106.6608 | 42.7868 | 6 | 215 | 161.25 | 97.376 | 38 | Power | 11.65 | 40.9665 | 4.6891 | 35.1672 | 5.8458 | 31.1368 | 29.1924 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
BFDTB1;DC SYS01 | NORTH EAST | BRADFORD | GIS Migrated | BFDTB1 | Power One PMP 25.48 V3.0 | 50 | 5 | 73.6 | 4.0112 | 2022-02-08 14:30 | 8.72 | 4.7088 | 7.63 | 3.6188 | 2 | PowerSafe | 2DDm50-13 | 5.2272 | 1.216 | 2 | 50 | 37.5 | 33.4888 | 96 |  | 0 | 4.7088 | 3.6188 | 54 | 47.4286 | 1.216 | 23.2629 | 37.5 | 4.0112 | 33.4888 | 0 | 33.4888 | 89.3035 |  | Single | 2DDm50-13 | 0 | 0 | 0 | 0 | 0 | 2DDm50-13
BFEC01;DC SYS01 | NORTHERN IRELAND | BELFAST | GIS Migrated | BFEC01 | Eaton Powerware APR48-ES | 36.6 | 26 | 266 | 14.497 | 2023-03-15 | 39.894 | 25.397 | 32.4275 | 17.9305 | 2 | PowerSafe | DDm100-33 | 28.1232 | 13.6262 | 5 | 72 | 54 | 39.503 | 12 |  | 18.4 | 6.997 | -0.4695 | 17.539 | -1.4478 | -4.7738 | -16.9746 | 54 | 14.497 | 39.503 | 18.4 | 21.103 | 39.0796 |  | Single | DDm100-33 | 0 | RA | 0 | 0 | 0 | DDm100-33
BFTN03;DC SYS01 | NORTHERN IRELAND | BELFAST | GIS MIGRATING | BFTN03 | Eaton Powerware APR48-ES | 36.6 | 25 | 467 | 25.4515 | 2023-03-15 | 38.2982 | 12.8467 | 21.7128 | -3.7387 | 3 | PowerSafe | DDm100-33 | 42.1848 | 16.7333 | 4 | 93 | 69.75 | 44.2985 | 19 |  | 14.2 | -1.3533 | -17.9387 | -3.5335 | -82.6181 | 2.5333 | 6.0052 | 69.75 | 25.4515 | 44.2985 | 14.2 | 30.0985 | 43.152 |  | Single | DDm100-33 | 0 | RA | 0 | 0 | 0 | DDm100-33
BHM;DC SYS02 | MIDLANDS | BIRMINGHAM | GIS Migrated - Capped | BHMN07 | Eaton Powerware APR48-ES | 36.6 | 31 | 405 | 22.0725 | 2023-02-07 | 47.8728 | 25.8003 | 38.041 | 15.9685 | 2 | PowerSafe | DDm125-33 | 35.5536 | 13.4811 | 2 | 12.6 | 9.45 | -12.6225 | 0 | P Core use only | 0 | 25.8003 | 15.9685 | 53.8934 | 41.9771 | 13.4811 | 37.9177 | 9.45 | 22.0725 | -12.6225 | 0 | -12.6225 | -133.5714 | Capped | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BHMN05;DC SYS A | MIDLANDS | BIRMINGHAM | GIS Migrated - Capped | BHMN05 | Eaton Powerware APR48-ES | 36.6 | 59 | 599 | 32.6455 | 2024-05-02 | 92.5541 | 59.9086 | 84.6276 | 51.9821 | 3 | PowerSafe | 2CP2000 | 48.0686 | 15.4231 | 9 | 110 | 82.5 | 49.8545 | 5 | Space | 1 | 58.9086 | 50.9821 | 63.6477 | 60.2429 | 14.4231 | 30.0053 | 82.5 | 32.6455 | 49.8545 | 1 | 48.8545 | 59.2176 | Capped | Dual | 2CP2000 | 0 | 0 | 0 | 0 | 0 | 2CP2000
BHMN05;DC SYS B | MIDLANDS | BIRMINGHAM | GIS Migrated - Capped | BHMN05 | Eaton Powerware APR48-ES | 36.6 | 59 | 677 | 36.8965 | 2024-05-02 | 92.5541 | 55.6576 | 82.9926 | 46.0961 | 3 | PowerSafe | DDm125-33 | 53.3304 | 16.4339 | 9 | 110 | 82.5 | 45.6035 | 5 | Space | 1 | 54.6576 | 45.0961 | 59.0547 | 54.3375 | 15.4339 | 28.9402 | 82.5 | 36.8965 | 45.6035 | 1 | 44.6035 | 54.0648 | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
BHMN08;DCSYS03A | MIDLANDS | BIRMINGHAM | GIS Migrated | BHMN08 | Eaton Powerware APR48-ES | 36.6 | 25 | 101 | 5.5045 | 2022-07-12 | 38.2982 | 32.7937 | 26.0728 | 20.5683 | 2 | PowerSafe | DDm125-33 | 35.5536 | 30.0491 | 2 | 60 | 45 | 39.4955 | 23 |  | 7.85 | 24.9437 | 12.7183 | 65.1303 | 48.78 | 22.1991 | 62.4384 | 45 | 5.5045 | 39.4955 | 7.85 | 31.6455 | 70.3233 |  | Dual | DDm125-33 | 0 | RA | PX | 0 | OPEX | DDm125-33
BHMN08;DCSYS03B | MIDLANDS | BIRMINGHAM | GIS Migrated | BHMN08 | Eaton Powerware APR48-ES | 36.6 | 25 | 138 | 7.521 | 2022-07-12 | 38.2982 | 30.7772 | 26.0728 | 18.5518 | 2 | PowerSafe | DDm125-33 | 35.5536 | 28.0326 | 2 | 60 | 45 | 37.479 | 23 |  | 8.28 | 22.4972 | 10.2718 | 58.7422 | 39.3966 | 19.7526 | 55.5572 | 45 | 7.521 | 37.479 | 8.28 | 29.199 | 64.8867 |  | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
BHMTF1;DC SYS A | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BHMTF1 | Eaton Powerware APR48-ES | 36.6 | 26 | 96 | 5.232 | 2024-05-02 | 39.894 | 34.662 | 28.0675 | 22.8355 | 2 | PowerSafe | DDm125-33 | 35.5536 | 30.3216 | 5 | 120 | 90 | 84.768 | 12 |  | 2.4 | 32.262 | 20.4355 | 80.8693 | 72.8084 | 27.9216 | 78.5338 | 90 | 5.232 | 84.768 | 2.4 | 82.368 | 91.52 |  | Dual | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
BHMTF1;DC SYS B | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BHMTF1 | Eaton Powerware APR48-ES | 36.6 | 25 | 123 | 6.7035 | 2024-05-02 | 38.2982 | 31.5947 | 26.0728 | 19.3693 | 2 | PowerSafe | DDm125-33 | 35.5536 | 28.8501 | 5 | 120 | 90 | 83.2965 | 12 |  | 2.5 | 29.0947 | 16.8693 | 75.9689 | 64.7008 | 26.3501 | 74.1137 | 90 | 6.7035 | 83.2965 | 2.5 | 80.7965 | 89.7739 |  | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
BHWCN1;DC SYS01 | LONDON | BOREHAMWOOD | Capped | BHWCN1 | Eaton Powerware NPR.48 | 55 | 9 | 194 | 10.573 | 2021-08-25 13:30 | 19.184 | 8.611 | 14.2517 | 3.6787 | 3 | PowerSafe | 2DDm85-15 | 15.1632 | 4.5902 | 3 | 20 | 15 | 4.427 | 0 | Space | 1 | 7.611 | 2.6787 | 39.6737 | 18.7959 | 3.5902 | 23.6771 | 15 | 10.573 | 4.427 | 1 | 3.427 | 22.8467 | Capped | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
BIFTS1; DC SYS01 | NORTH WEST | BARROW-IN-FURNESS | GIS Migrated - Capped | BIFTS1 | Power One PMP 11.48 | 23 | 6 | 39 | 2.1255 | 2024-03-05 | 5.014 | 2.8885 | 5.995 | 3.8695 | 5 | Enersys | SBS C11F | 4.32 | 2.1945 | 1 | 5 | 3.75 | 1.6245 | 0 | Space; Power; Air Con | 0 | 2.8885 | 3.8695 | 57.6087 | 64.5455 | 2.1945 | 50.7986 | 3.75 | 2.1255 | 1.6245 | 0 | 1.6245 | 43.32 | Capped | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
BKBN41;DC SYS01 | NORTH WEST | BLACKBURN | GIS Migrated | BKBN41 | Eaton Powerware APR48-ES | 36.6 | 9 | 60 | 3.27 | 2024-05-02 | 12.7661 | 9.4961 | 9.4721 | 6.2021 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 6.8388 | 3 | 30 | 22.5 | 19.23 | 20 |  | 3 | 6.4961 | 3.2021 | 50.8855 | 33.8056 | 3.8388 | 37.9748 | 22.5 | 3.27 | 19.23 | 3 | 16.23 | 72.1333 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
BKLN05;DC SYS02 | THAMES VALLEY | BRACKNELL | GIS Migrated | BKLN05 | Eaton Powerware APR48-ES | 36.6 | 61 | 1155.5 | 62.9748 | 2024-05-03 | 95.7456 | 32.7709 | 86.982 | 24.0072 | 3 | PowerSafe | DDm125-33 | 53.3304 | -9.6444 | 12 | 495 | 371.25 | 308.2753 | 104 |  | 37.8 | -5.0291 | -13.7927 | -5.2526 | -15.857 | -47.4444 | -88.963 | 413.5 | 198.4345 | 215.0655 | 121.45 | 93.6155 | 22.6398 |  | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BKLN05;DC SYS03;NEAR CK | THAMES VALLEY | BRACKNELL | GIS Migrated | BKLN05 | Eaton Powerware APR48-ES | 36.6 | 57 | 1155.5 | 62.9748 | 2024-05-03 | 89.3626 | 26.3878 | 46.3032 | -16.6715 | 6 | PowerSafe | DDm125-33 | 106.6608 | 43.6861 | 12 | 495 | 371.25 | 308.2753 | 104 |  | 21 | 5.3878 | -37.6715 | 6.0292 | -81.3584 | 22.6861 | 21.2693 | [7 empty] | Dual | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BKLN05;DC SYS04a | THAMES VALLEY | BRACKNELL | GIS Migrated | BKLN05 Ext | Eaton Powerware NPR.48 | 55 | 102 | 1330 | 72.485 | 2024-05-02 | 242.198 | 169.713 | 171.9475 | 99.4625 | 12 | PowerSafe | DDm125-33 | 213.3216 | 140.8366 | 10 | 664 | 498 | 425.515 | 23 |  | 62.65 | 107.063 | 36.8125 | 44.2047 | 21.4092 | 78.1866 | 36.652 | [7 empty] | Dual | DDm125-33 | P-Core |  |  |  | OPEX | DDm125-33
BKLN05;DC SYS04b | THAMES VALLEY | BRACKNELL | GIS Migrated | BKLN05 | Eaton Powerware HDR48-ES | 55 | 102 | 1059 | 57.7155 | 2024-05-02 | 242.198 | 184.4825 | 171.9475 | 114.232 | 12 | PowerSafe | DDm125-33 | 213.3216 | 155.6061 | 12 | 495 | 371.25 | 313.5345 | 104 |  | 62.65 | 121.8325 | 51.582 | 50.3029 | 29.9987 | 92.9561 | 43.5756 | 371.25 | 57.7155 | 313.5345 | 62.65 | 250.8845 | 67.5783 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
BMGV03; DC SYS A | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BMGV03 | Dummy Type 100A | 100 | 9 | 115 | 6.2675 | 2021-10-29 10:00 | 34.88 | 28.6125 | 26.16 | 19.8925 | 2 | PowerSafe | DDm100-33 | 28.1232 | 21.8557 | 4 | 90 | 67.5 | 61.2325 | 30 |  | 0 | 28.6125 | 19.8925 | 82.0312 | 76.0417 | 21.8557 | 77.7141 | 67.5 | 19.5655 | 47.9345 | 0 | 47.9345 | 71.0141 |  | Dual | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
BMGV03; DC SYS B | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BMGV03 | Dummy Type 100A | 100 | 9 | 244 | 13.298 | 2021-10-29 12:00 | 34.88 | 21.582 | 26.16 | 12.862 | 2 | PowerSafe | DDm100-33 | 28.1232 | 14.8252 | 4 | 90 | 67.5 | 54.202 | 30 |  | 0 | 21.582 | 12.862 | 61.875 | 49.1667 | 14.8252 | 52.7152 | [7 empty] | Dual | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
BMTDN1;DC SYS01 | SOUTH | BOURNEMOUTH | GIS Migrated - Capped | BMTDN1 | Eltek E1333 | 27.8 | 8 | 105 | 5.7225 | 2022-11-14 | 8.4846 | 2.7621 | 9.1931 | 3.4706 | 2 | Yuasa | EN160 | 2.916 | -2.8065 | 2 | 15 | 11.25 | 5.5275 | 2 | Space | 0.5 | 2.2621 | 2.9706 | 26.6609 | 32.3131 | -3.3065 | -113.3916 | 11.25 | 5.7225 | 5.5275 | 0.5 | 5.0275 | 44.6889 | Capped | Single | EN160 | 0 | 0 | 0 | 0 | 0 | EN160
BPL;DC SYS01 | NORTH WEST | BLACKPOOL | GIS Migrated | BPL | Eaton Powerware APR48-ES | 36.6 | 6 | 51 | 2.7795 | 2024-05-02 | 7.9788 | 5.1993 | 6.1585 | 3.379 | 7 | PowerSafe | 12V101F (4 hour Rate) | 6.2748 | 3.4953 | 3 | 8 | 6 | 3.2205 | 6 |  | 5.4 | -0.2007 | -2.021 | -2.5154 | -32.8164 | -1.9047 | -30.3548 | 6 | 2.7795 | 3.2205 | 5.4 | -2.1795 | -36.325 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
BRETS1;DC SYS01 | SCOTLAND | BRECHIN | Redstream Optical Network Site | BRETS1 | Powec Dummy 20A | 20 | 4 | 2 | 0.109 | 2021-12-08 13:10 | 2.616 | 2.507 | 2.398 | 2.289 | 2 | Enersys | 12V100F | 1.9526 | 1.8436 | 2 | 6.7 | 5.025 | 4.916 | 9 |  | 0.5 | 2.007 | 1.789 | 76.7202 | 74.6038 | 1.3436 | 68.8115 | 5.025 | 0.109 | 4.916 | 0.5 | 4.416 | 87.8806 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
BRRTS1; DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | BRORA | Redstream Optical Network Site | BRRTS1 | Eaton Powerware APR48-ES | 36.6 | 2 | 13 | 0.7085 | 2024-05-02 | 1.5958 | 0.88726 | -0.11445 | -0.82295 | 3 | Enersys | 12V155F | 4.212 | 3.5035 | 1 | 5 | 3.75 | 3.0415 | 1 |  | 0.4 | 0.48726 | -1.223 | 30.5347 | 1068.5438 | 3.1035 | 73.6823 | 3.75 | 0.7085 | 3.0415 | 0.4 | 2.6415 | 70.44 |  | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
BSG;DC SYS01 | THAMES VALLEY | BASINGSTOKE | Redstream Optical Network Site | BSG | Eaton Powerware APR48-ES | 36.6 | 21 | 287 | 15.6415 | 2023-06-14 | 31.9152 | 16.2737 | 22.454 | 6.8125 | 2 | PowerSafe | DDm100-33 | 28.1232 | 12.4817 | 3 | 44 | 33 | 17.3585 | 57 |  | 4 | 12.2737 | 2.8125 | 38.4572 | 12.5256 | 8.4817 | 30.1591 | 33 | 15.6415 | 17.3585 | 4 | 13.3585 | 40.4803 |  | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
BSH;DC SYS01;GND | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN07 | Eaton Powerware APR48-ES | 36.6 | 57 | 580 | 31.61 | 2024-03-05 | 87.7668 | 56.1568 | 44.3085 | 12.6985 | 6 | PowerSafe | DDm125-33 | 106.6608 | 75.0508 | 4 | 135 | 101.25 | 69.64 | 31 |  | 20.8 | 35.3568 | -8.1015 | 40.2849 | -18.2843 | 54.2508 | 50.8629 | 101.25 | 31.61 | 69.64 | 20.8 | 48.84 | 48.237 |  | Single | DDm125-33 | P-Core | RA | PX | 0 | 0 | DDm125-33
BSH;DC SYS02;GND | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN07 | Eaton Powerware APR48-ES | 36.6 | 57 | 1135 | 61.8575 | 2024-04-02 | 87.7668 | 25.9093 | 44.3085 | -17.549 | 6 | PowerSafe | DDm125-33 | 106.6608 | 44.8033 | 4 | 135 | 101.25 | 39.3925 | 31 |  | 23.3 | 2.6093 | -40.849 | 2.973 | -92.1922 | 21.5033 | 20.1605 | 101.25 | 61.8575 | 39.3925 | 23.3 | 16.0925 | 15.8938 |  | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BSH;DC SYS03;GND | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN07 | Eaton Powerware APR48-ES | 36.6 | 57 | 807 | 43.9815 | 2024-05-02 | 87.7668 | 43.7853 | 66.1085 | 22.127 | 4 | PowerSafe | DDm125-33 | 71.1072 | 27.1257 | 4 | 135 | 101.25 | 57.2685 | 31 |  | 3.6 | 40.1853 | 18.527 | 45.7864 | 28.0251 | 23.5257 | 33.0848 | 101.25 | 43.9815 | 57.2685 | 3.6 | 53.6685 | 53.0059 |  | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BSHN03;DC SYS A | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN03 | Eaton Powerware NPR.48 | 55 | 88 | 1300 | 70.85 | 2024-05-02 | 208.626 | 137.776 | 198.6525 | 127.8025 | 6 | PowerSafe | 2CP2000 | 96.1373 | 25.2873 | 13 | 540 | 405 | 334.15 | 130 |  | 16.6 | 121.176 | 111.2025 | 58.0829 | 55.9784 | 8.6873 | 9.0363 | 405 | 146.605 | 258.395 | 31.2 | 227.195 | 56.0975 |  | Single | 2CP2000 | 0 | 0 | 0 | 0 | 0 | 2CP2000
BSHN03;DC SYS B | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN03 | Eaton Powerware NPR.48 | 55 | 88 | 1390 | 75.755 | 2024-05-02 | 208.626 | 132.871 | 198.6525 | 122.8975 | 6 | PowerSafe | 2CP2000 | 96.1373 | 20.3823 | 13 | 540 | 405 | 329.245 | 130 |  | 14.6 | 118.271 | 108.2975 | 56.6904 | 54.5161 | 5.7823 | 6.0146 | [7 empty] | Single | 2CP2000 | 0 | 0 | 0 | 0 | 0 | 2CP2000
BTFTB1;DC SYS01 | LONDON | BRENTFORD | GIS Migrated - Capped | BTFTB1 | Eaton Powerware APR48-ES | 36.6 | 53 | 1219 | 66.4355 | 2024-05-02 | 82.9795 | 16.544 | 60.1244 | -6.3111 | 5 | PowerSafe | DDm100-33 | 70.308 | 3.8725 | 5 | 186 | 139.5 | 73.0645 | 18 | Power; Autonomy | 0 | 16.544 | -6.3111 | 19.9375 | -10.4967 | 3.8725 | 5.5079 | 139.5 | 66.4355 | 73.0645 | 0 | 73.0645 | 52.376 | Capped | Single | DDm100-33 | P-Core | 0 | 0 | 0 | 0 | DDm100-33
BTFTB1;DC SYS02 | LONDON | BRENTFORD | GIS Migrated - Capped | BTFTB1 | Eaton Powerware APR48-ES | 36.6 | 61 | 605 | 32.9725 | 2024-05-02 | 95.7456 | 62.7731 | 65.182 | 32.2095 | 5 | PowerSafe | DDm125-33 | 88.884 | 55.9115 | 5 | 186 | 139.5 | 106.5275 | 18 | Power; Autonomy | 32.45 | 30.3231 | -0.2405 | 31.6705 | -0.36897 | 23.4615 | 26.3956 | 139.5 | 32.9725 | 106.5275 | 32.45 | 74.0775 | 53.1022 | Capped | Single | DDm125-33 | 0 | RA | PX | 0 | OPEX | DDm125-33
BTLCD1;DC SYS01 | SOUTH WEST | BRISTOL | GIS Migrated - Capped | BTLCD1 | Eaton Powerware NPR.48 | 55 | 29 | 748 | 40.766 | 2023-03-02 | 67.144 | 26.378 | 49.05 | 8.284 | 4 | PowerSafe | DDm100-33 | 56.2464 | 15.4804 | 5 | 117 | 87.75 | 46.984 | 45 | DC Dist | 2.25 | 24.128 | 6.034 | 35.9347 | 12.3017 | 13.2304 | 23.5222 | 87.75 | 40.766 | 46.984 | 2.25 | 44.734 | 50.9789 | Capped | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
BTLN08;DC SYS01 | SOUTH WEST | BRISTOL | GIS Migrated - Capped | BTLN08 | Eaton Powerware APR48-ES | 36.6 | 41 | 1061 | 57.8245 | 2023-03-16 | 63.8304 | 6.0059 | 36.188 | -21.6365 | 4 | PowerSafe | DDm125-33 | 71.1072 | 13.2827 | 8 | 126 | 94.5 | 36.6755 | 14 | Autonomy | 5 | 1.0059 | -26.6365 | 1.5759 | -73.6059 | 8.2827 | 11.6482 | 94.5 | 57.8245 | 36.6755 | 5 | 31.6755 | 33.519 | Capped | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
BTLN09;DC SYS01 | SOUTH WEST | BRISTOL | GIS Migrated | BTLN09 | Eaton Powerware APR48-ES | 36.6 | 56 | 573 | 31.2285 | 2024-05-03 | 87.7668 | 56.5383 | 55.2085 | 23.98 | 5 | PowerSafe | DDm125-33 | 88.884 | 57.6555 | 5 | 142 | 106.5 | 75.2715 | 20 |  | 48.13 | 8.4083 | -24.15 | 9.5803 | -43.7433 | 9.5255 | 10.7168 | 106.5 | 31.2285 | 75.2715 | 48.13 | 27.1415 | 25.485 |  | Single | DDm125-33 | 0 | RA | PX | AM | OPEX | DDm125-33
BTN-DCSYS01 | SOUTH | BRIGHTON | GIS MIGRATING | BTN | Eaton Powerware APR48-ES | 36.6 | 33 | 348 | 18.966 | 2021-10-22 16:30 | 51.0643 | 32.0983 | 34.1824 | 15.2164 | 4 | PowerSafe | DDm85-33 | 45.9648 | 26.9988 | 3 | 80 | 60 | 41.034 | 59 |  | 2.7 | 29.3983 | 12.5164 | 57.5712 | 36.6165 | 24.2988 | 52.8639 | 60 | 18.966 | 41.034 | 2.7 | 38.334 | 63.89 |  | Single | DDm85-33 | 0 | RA | 0 | 0 | 0 | DDm85-33
BTNW01;DC SYS01 | MIDLANDS | BARTON | GIS Migrated - Capped | BTNW01 | Eaton Powerware APR48-ES | 36.6 | 8 | 75 | 4.0875 | 2024-05-02 | 11.1703 | 7.0828 | 8.5129 | 4.4254 | 10 | PowerSafe | 12V101F (4 hour Rate) | 8.964 | 4.8765 | 2 | 9.2 | 6.9 | 2.8125 | 1 | Space | 0 | 7.0828 | 4.4254 | 63.4075 | 51.9846 | 4.8765 | 54.4009 | 6.9 | 4.0875 | 2.8125 | 0 | 2.8125 | 40.7609 | Capped | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
BTRTP1;DC SYS01 | SCOTLAND | GLASGOW | Redstream Optical Network Site | BTRTP1 | Eaton Powerware APR48-ES | 36.6 | 19 | 144 | 7.848 | 2024-05-02 | 28.7237 | 20.8757 | 18.4646 | 10.6166 | 2 | PowerSafe | DDm100-33 | 28.1232 | 20.2752 | 5 | 120 | 90 | 82.152 | 3 |  | 0 | 20.8757 | 10.6166 | 72.6776 | 57.497 | 20.2752 | 72.0942 | 90 | 7.848 | 82.152 | 0 | 82.152 | 91.28 |  | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
BYR;DC SYS01 | NORTHERN IRELAND | BALLYWATER | GIS MIGRATING | BYR | Duvine DD686 | 75 | 2 | 5 | 0.2725 | 2022-11-08 | 3.27 | 2.9975 | 1.9075 | 1.635 | 4 | PowerSafe | 12V101F (4 hour Rate) | 3.5856 | 3.3131 | 4 | 15 | 11.25 | 10.9775 | 4 |  | 0 | 2.9975 | 1.635 | 91.6667 | 85.7143 | 3.3131 | 92.4002 | 11.25 | 0.2725 | 10.9775 | 0 | 10.9775 | 97.5778 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
CAMN02;DC SYS01 | ANGLIA | CAMBRIDGE | GIS Migrated - Capped | CAMN02 | Duvine DD686 | 75 | 6 | 140 | 7.63 | 2022-05-05 13:00 | 16.35 | 8.72 | 10.7093 | 3.0793 | 3 | PowerSafe | 2DDm85-15 | 15.1632 | 7.5332 | 3 | 30 | 22.5 | 14.87 | 1 | Space | 1 | 7.72 | 2.0793 | 47.2171 | 19.4155 | 6.5332 | 43.0859 | 22.5 | 7.63 | 14.87 | 1 | 13.87 | 61.6444 | Capped | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
CAMN41;DC SYS01 | ANGLIA | CAMBRIDGE | GIS Migrated | CAMN41 | Eaton Powerware APR48-ES | 36.6 | 9 | 69 | 3.7605 | 2022-02-04 13:00 | 12.7661 | 9.0056 | 9.4721 | 5.7116 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 6.3483 | 2 | 15 | 11.25 | 7.4895 | 12 |  | 0 | 9.0056 | 5.7116 | 70.543 | 60.2992 | 6.3483 | 62.7997 | 11.25 | 3.7605 | 7.4895 | 0 | 7.4895 | 66.5733 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
CBY;DC SYS01 | SOUTH EAST | CANTERBURY | Redstream Optical Network Site | CBY | Eaton Powerware APR48-ES | 36.6 | 15 | 132 | 7.194 | 2021-09-09 17:00 | 22.3406 | 15.1466 | 14.0283 | 6.8343 | 5 | PowerSafe | 2DDm85-13 | 21.816 | 14.622 | 4 | 22.5 | 16.875 | 9.681 | 13 |  | 1 | 14.1466 | 5.8343 | 63.3224 | 41.5895 | 13.622 | 62.4404 | 16.875 | 7.194 | 9.681 | 1 | 8.681 | 51.443 |  | Single | 2DDm85-13 | 0 | 0 | 0 | 0 | 0 | 2DDm85-13
CDFN02;DC SYS01 | WALES | CARDIFF | GIS Migrated | CDFN02 | Eaton Powerware APR48-ES | 36.6 | 27 | 321 | 17.4945 | 2024-05-02 | 41.4898 | 23.9953 | 30.0622 | 12.5677 | 2 | PowerSafe | DDm125-33 | 35.5536 | 18.0591 | 3 | 30 | 22.5 | 5.0055 | 15 |  | 3 | 20.9953 | 9.5677 | 50.6035 | 31.8263 | 15.0591 | 42.356 | 22.5 | 17.4945 | 5.0055 | 3 | 2.0055 | 8.9133 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
CELL01;DC SYS01 | MIDLANDS | STOKE-ON-TRENT | GIS Migrated | CELL01 | Eaton Powerware APR48-ES | 36.6 | 5 | 39 | 2.1255 | 2021-11-01 11:00 | 6.383 | 4.2575 | 4.4908 | 2.3653 | 8 | Enersys | 12V100F | 7.8106 | 5.6851 | 2 | 8 | 6 | 3.8745 | 8 |  | 0 | 4.2575 | 2.3653 | 66.7008 | 52.6699 | 5.6851 | 72.7868 | 6 | 2.1255 | 3.8745 | 0 | 3.8745 | 64.575 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
CFDTN1;DC SYS01 | ANGLIA | CHELMSFORD | Redstream Optical Network Site | CFDTN1 | Eaton Powerware APR48-ES | 36.6 | 16 | 220 | 11.99 | 2023-05-12 | 23.9364 | 11.9464 | 0.2725 | -11.7175 | 4 | PowerSafe | DDm85-33 | 45.9648 | 33.9748 | 2 | 22 | 16.5 | 4.51 | 6 |  | 1.5 | 10.4464 | -13.2175 | 43.6423 | -4850.4587 | 32.4748 | 70.6515 | 16.5 | 11.99 | 4.51 | 1.5 | 3.01 | 18.2424 |  | Single | DDm85-33 | 0 | 0 | 0 | 0 | 0 | DDm85-33
CHDCD1;DC SYS01 | NORTH EAST | CHESTERFIELD | Capped | CHDCD1 | Eaton Powerware APR48-ES | 36.6 | 11 | 78 | 4.251 | 2024-05-02 | 15.9576 | 11.7066 | 14.388 | 10.137 | 2 | PowerSafe | 2DDm85-13 | 8.7264 | 4.4754 | 2 | 8 | 6 | 1.749 | 0 | Space | 0 | 11.7066 | 10.137 | 73.3607 | 70.4545 | 4.4754 | 51.2858 | 6 | 4.251 | 1.749 | 0 | 1.749 | 29.15 | Capped | Single | 2DDm85-13 | 0 | 0 | 0 | 0 | 0 | 2DDm85-13
CHMN21;DC SYS01 | SOUTH WEST | CHELTENHAM | GIS Migrated | CHMN21 | Eaton Powerware APR48-ES | 36.6 | 7 | 41 | 2.2345 | 2024-05-02 | 9.5746 | 7.3401 | 5.4827 | 3.2482 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 7.8743 | 2 | 15 | 11.25 | 9.0155 | 25 |  | 0 | 7.3401 | 3.2482 | 76.6621 | 59.2445 | 7.8743 | 77.8955 | 11.25 | 2.2345 | 9.0155 | 0 | 9.0155 | 80.1378 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
CHTN07;DC SYS01 | LONDON | LONDON | GIS Migrated - Capped | CHTN07 | Duvine DD686 | 75 | 28 | 780 | 42.51 | 2023-10-12 | 88.29 | 45.78 | 77.6625 | 35.1525 | 3 | PowerSafe | DDm125-33 | 53.3304 | 10.8204 | 9 | 240 | 180 | 137.49 | 18 | Space | 15.5 | 30.28 | 19.6525 | 34.2961 | 25.305 | -4.6796 | -8.7747 | 180 | 142.245 | 37.755 | 17 | 20.755 | 11.5306 | Capped | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
CHTN07;DC SYS02 | LONDON | LONDON | GIS Migrated - Capped | CHTN07 | Eaton Powerware NPR.48 | 55 | 54 | 1830 | 99.735 | 2023-10-12 | 127.094 | 27.359 | 93.4675 | -6.2675 | 6 | PowerSafe | DDm125-33 | 106.6608 | 6.9258 | 9 | 240 | 180 | 80.265 | 18 | Space | 1.5 | 25.859 | -7.7675 | 20.3464 | -8.3104 | 5.4258 | 5.087 | [6 empty] | Capped | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
CHTTN3;DC SYS01A | LONDON | LONDON | GIS Migrated | CHTTN3 | Eaton Powerware APR48-ES | 36.6 | 39 | 293 | 15.9685 | 2022-08-31 | 60.6389 | 44.6704 | 43.0986 | 27.1301 | 3 | PowerSafe | DDm125-33 | 53.3304 | 37.3619 | 6 | 262 | 196.5 | 180.5315 | 65 |  | 7.8 | 36.8704 | 19.3301 | 60.8032 | 44.8509 | 29.5619 | 55.4316 | 196.5 | 31.392 | 165.108 | 16.2 | 148.908 | 75.7802 |  | Dual | DDm125-33 | 0 | RA | PX | 0 | OPEX | DDm125-33
CHTTN3;DC SYS01B | LONDON | LONDON | GIS Migrated | CHTTN3 | Eaton Powerware APR48-ES | 36.6 | 39 | 283 | 15.4235 | 2023-02-22 | 60.6389 | 45.2154 | 43.0986 | 27.6751 | 3 | PowerSafe | DDm125-33 | 53.3304 | 37.9069 | 6 | 262 | 196.5 | 181.0765 | 65 |  | 8.4 | 36.8154 | 19.2751 | 60.7125 | 44.7233 | 29.5069 | 55.3285 | [7 empty] | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
CKNN03-DCSYS01a | SOUTH WEST | CREWKERNE | Redstream Optical Network Site | CKNN03 | Eaton Powerware APR48-ES | 36.6 | 18 | 35 | 1.9075 | 2024-05-02 | 27.1279 | 25.2204 | 22.7919 | 20.8844 | 2 | PowerSafe | DDm85-25 | 17.4096 | 15.5021 | 6 | 150 | 112.5 | 110.5925 | 24 |  | 6.9 | 18.3204 | 13.9844 | 67.5334 | 61.3569 | 8.6021 | 49.4101 | 112.5 | 1.9075 | 110.5925 | 6.9 | 103.6925 | 92.1711 |  | Dual | DDm85-25 | 0 | 0 | 0 | AM | 0 | DDm85-25
CKNN03-DCSYS01b | SOUTH WEST | CREWKERNE | Redstream Optical Network Site | CKNN03 | Eaton Powerware APR48-ES | 36.6 | 18 | 54 | 2.943 | 2024-05-02 | 27.1279 | 24.1849 | 22.7919 | 19.8489 | 2 | PowerSafe | DDm85-25 | 17.4096 | 14.4666 | 6 | 150 | 112.5 | 109.557 | 24 |  | 6.8 | 17.3849 | 13.0489 | 64.085 | 57.2524 | 7.6666 | 44.0366 | 112.5 | 2.943 | 109.557 | 6.8 | 102.757 | 91.3396 |  | Dual | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
COV;DC SYS01a | MIDLANDS | COVENTRY | Redstream Optical Network Site | COV | Eaton Powerware HDR48-ES | 55 | 23 | 296 | 16.132 | 2023-10-24 | 52.756 | 36.624 | 33.245 | 17.113 | 3 | PowerSafe | DDm125-33 | 53.3304 | 37.1984 | 11 | 120 | 90 | 73.868 | 17 |  | 9.35 | 27.274 | 7.763 | 51.6984 | 23.3509 | 27.8484 | 52.2186 | 90 | 32.482 | 57.518 | 18.7 | 38.818 | 43.1311 |  | Dual | DDm125-33 | 0 | 0 | 0 | 0 | OPEX | DDm125-33
COV;DC SYS01b | MIDLANDS | COVENTRY | Redstream Optical Network Site | COV | Eaton Powerware HDR48-ES | 55 | 23 | 300 | 16.35 | 2023-10-24 | 52.756 | 36.406 | 33.245 | 16.895 | 3 | PowerSafe | DDm125-33 | 53.3304 | 36.9804 | 11 | 120 | 90 | 73.65 | 17 |  | 9.35 | 27.056 | 7.545 | 51.2852 | 22.6951 | 27.6304 | 51.8098 | [7 empty] | Dual | DDm125-33 | [5 empty] | DDm125-33
COWL02;DC SYS01 | THAMES VALLEY | COWLEY | GIS Migrated | COWL02 | Eaton Powerware APR48-3G | 37.5 | 8 | 64 | 3.488 | 2024-05-02 | 11.445 | 7.957 | 9.5648 | 6.0767 | 10 | Enersys | 12V105F | 8.964 | 5.476 | 2 | 14 | 10.5 | 7.012 | 7 |  | 0 | 7.957 | 6.0767 | 69.5238 | 63.5328 | 5.476 | 61.0888 | 10.5 | 3.488 | 7.012 | 0 | 7.012 | 66.781 |  | Single | 12V105F | 0 | 0 | 0 | 0 | 0 | 12V105F
CSLN13;DC SYS01 | NORTH WEST | CARLISLE | GIS Migrated | CSLN13 | Eaton Powerware APR48-ES | 36.6 | 9 | 123 | 6.7035 | 2024-05-02 | 12.7661 | 6.0626 | 9.4721 | 2.7686 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 3.4053 | 3 | 40 | 30 | 23.2965 | 8 |  | 1 | 5.0626 | 1.7686 | 39.6565 | 18.6717 | 2.4053 | 23.7941 | 30 | 6.7035 | 23.2965 | 1 | 22.2965 | 74.3217 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
CTNN01-DCSYS01a | SOUTH WEST | CREDITON | Redstream Optical Network Site | CTNN01 | Eaton Powerware APR48-ES | 36.6 | 17 | 65 | 3.5425 | 2024-05-02 | 25.5322 | 21.9897 | 20.7972 | 17.2547 | 2 | PowerSafe | DDm85-25 | 17.4096 | 13.8671 | 4 | 66 | 49.5 | 45.9575 | 20 |  | 6.8 | 15.1897 | 10.4547 | 59.4923 | 50.2697 | 7.0671 | 40.5931 | 49.5 | 4.796 | 44.704 | 13.7 | 31.004 | 62.6343 |  | Dual | DDm85-25 | 0 | 0 | 0 | AM | 0 | DDm85-25
CTNN01-DCSYS01b | SOUTH WEST | CREDITON | Redstream Optical Network Site | CTNN01 | Eaton Powerware APR48-ES | 36.6 | 17 | 23 | 1.2535 | 2024-05-02 | 25.5322 | 24.2787 | 20.7972 | 19.5437 | 2 | PowerSafe | DDm85-25 | 17.4096 | 16.1561 | 4 | 66 | 49.5 | 48.2465 | 20 |  | 6.9 | 17.3787 | 12.6437 | 68.0658 | 60.7952 | 9.2561 | 53.1666 | [7 empty] | Dual | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
CTRTK1;DC SYS01 | NORTH WEST | CHESTER | GIS Migrated | CTRTK1 | Power One PMP 25.48 V3.0 | 50 | 12 | 54.7 | 2.9811 | 2022-02-02 17:00 | 23.98 | 20.9989 | 23.4895 | 20.5084 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 7.1276 | 4 | 22.5 | 16.875 | 13.8939 | 7 |  | 0 | 20.9989 | 20.5084 | 87.5682 | 87.3086 | 7.1276 | 70.5094 | 16.875 | 2.9811 | 13.8939 | 0 | 13.8939 | 82.3339 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
CTRTS1; DC SYS01 | NORTH WEST | CHESTER | GIS Migrated | CTRTS1 | Eaton Powerware APR48-ES | 36.6 | 9 | 153 | 8.3385 | 2024-05-02 | 12.7661 | 4.4276 | 9.4721 | 1.1336 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 1.7703 | 2 | 25 | 18.75 | 10.4115 | 51 |  | 4 | 0.42758 | -2.8664 | 3.3493 | -30.2615 | -2.2297 | -22.057 | 18.75 | 8.3385 | 10.4115 | 4 | 6.4115 | 34.1947 |  | Single | 2DDm85-15 | 0 | RA | 0 | 0 | 0 | 2DDm85-15
CYNTN2;DC SYS01 | LONDON | CROYDON | Capped | CYNTN2(EXT'N) | Duvine DD686 | 75 | 28 | 900 | 49.05 | 2023-07-20 | 88.29 | 39.24 | 66.7625 | 17.7125 | 5 | PowerSafe | DDm100-33 | 70.308 | 21.258 | 3 | 60 | 45 | -4.05 | 6 | Space | 3 | 36.24 | 14.7125 | 41.0466 | 22.0371 | 18.258 | 25.9686 | 72 | 49.05 | 22.95 | 3 | 19.95 | 27.7083 | Capped | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
DBY;DC SYS01 | MIDLANDS | DERBY | Redstream Optical Network Site | DBY | Eaton Powerware APR48-ES | 36.6 | 19 | 225 | 12.2625 | 2021-11-30 17:00 | 28.7237 | 16.4612 | 23.7402 | 11.4777 | 2 | FIAMM | 2SLA1500 | 25.0128 | 12.7503 | 6 | 43 | 32.25 | 19.9875 | 18 |  | 1 | 15.4612 | 10.4777 | 53.8273 | 44.1348 | 11.7503 | 46.9771 | 32.25 | 12.2625 | 19.9875 | 1 | 18.9875 | 58.876 |  | Single | 2SLA1500 | 0 | 0 | 0 | 0 | 0 | 2SLA1500
DCT;DC SYS01 | THAMES VALLEY | DIDCOT | Redstream Optical Network Site | DCT | Eaton Powerware NPR.48 | 55 | 8 | 79 | 4.3055 | 2023-04-28 | 16.786 | 12.4805 | 14.6256 | 10.3201 | 3 | Yuasa | EN480-2 | 13.1544 | 8.8489 | 6 | 60 | 45 | 40.6945 | 11 |  | 4.4 | 8.0805 | 5.9201 | 48.1383 | 40.4777 | 4.4489 | 33.8206 | 45 | 4.3055 | 40.6945 | 4.4 | 36.2945 | 80.6544 |  | Single | EN480-2 | 0 | 0 | 0 | 0 | 0 | EN480-2
DFSN01; DC SYS01 | SCOTLAND | DUMFRIES | GIS Migrated | DFSN01 | Eaton Powerware APR48-ES | 36.6 | 8 | 116 | 6.322 | 2024-04-02 | 11.1703 | 4.8483 | 11.5104 | 5.1884 | 3 | PowerSafe | SBS XL 150F-FT | 11.6899 | 5.3679 | 2 | 14 | 10.5 | 4.178 | 47 |  | 1 | 3.8483 | 4.1884 | 34.4513 | 36.388 | 4.3679 | 37.3648 | 10.5 | 6.322 | 4.178 | 1 | 3.178 | 30.2667 |  | Single | SBS XL 150F-FT | 0 | 0 | 0 | 0 | 0 | SBS XL 150F-FT
DFSNC1; DC SYS01 | SCOTLAND | DUMFRIES | Redstream Optical Network Site | DFSNC1 | Power One PMP 10.48 SIC | 22 | 6 | 33 | 1.7985 | 2021-09-06 09:10 | 4.796 | 2.9975 | 5.8315 | 4.033 | 3 | PowerSafe | SBS 12V100F | 2.8253 | 1.0268 | 2 | 10 | 7.5 | 5.7015 | 0 |  | 0 | 2.9975 | 4.033 | 62.5 | 69.1589 | 1.0268 | 36.3426 | 7.5 | 1.7985 | 5.7015 | 0 | 5.7015 | 76.02 |  | Single | SBS 12V100F | 0 | 0 | 0 | 0 | 0 | SBS 12V100F
DGS;DC SYS01 | NORTH WEST | DOUGLAS | Redstream Optical Network Site | DGS | Duvine DD686 | 75 | 6 | 76 | 4.142 | 2024-05-02 | 16.35 | 12.208 | 16.7315 | 12.5895 | 4 | Enersys | 12v170FS | 6.601 | 2.459 | 3 | 10 | 7.5 | 3.358 | 3 |  | 0 | 12.208 | 12.5895 | 74.6667 | 75.2443 | 2.459 | 37.2516 | 7.5 | 4.142 | 3.358 | 0 | 3.358 | 44.7733 |  | Single | 12v170FS | 0 | 0 | 0 | 0 | 0 | 12v170FS
DHMNU1;DC SYS01 | NORTH EAST | DURHAM | GIS Migrated | DHMNU1 | Power One PMP 25.48 V3.0 | 50 | 5 | 40 | 2.18 | 2022-01-13 13:00 | 8.72 | 6.54 | 8.284 | 6.104 | 6 | Enersys | 12V100F | 5.8579 | 3.6779 | 2 | 15 | 11.25 | 9.07 | 1 |  | 0 | 6.54 | 6.104 | 75 | 73.6842 | 3.6779 | 62.7854 | 11.25 | 2.18 | 9.07 | 0 | 9.07 | 80.6222 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
DKTN08; DC SYS01 | LONDON | LONDON | Redstream Optical Network Site | DKTN08 | Eaton Powerware APR48-ES | 36.6 | 49 | 938 | 51.121 | 2024-04-16 | 76.5965 | 25.4755 | 52.1456 | 1.0246 | 4 | PowerSafe | DDm125-33 | 71.1072 | 19.9862 | 6 | 200 | 150 | 98.879 | 33 |  | 7.4 | 18.0755 | -6.3754 | 23.5983 | -12.2262 | 12.5862 | 17.7003 | 150 | 51.121 | 98.879 | 7.4 | 91.479 | 60.986 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
DLD;DC SYS01 | SCOTLAND | DUNDONALD | Redstream Optical Network Site | DLD | Eaton Powerware APR48-ES | 36.6 | 6 | 52 | 2.834 | 2024-05-02 | 7.9788 | 5.1448 | 6.7035 | 3.8695 | 6 | PowerSafe | 12V101F (4 hour Rate) | 5.3784 | 2.5444 | 3 | 10 | 7.5 | 4.666 | 11 |  | 0 | 5.1448 | 3.8695 | 64.4809 | 57.7236 | 2.5444 | 47.3077 | 7.5 | 2.834 | 4.666 | 0 | 4.666 | 62.2133 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
DLNTC1;DC SYS01 | NORTH EAST | DARLINGTON | Redstream Optical Network Site | DLNTC1 | Power One PMP 25.48 V3.0 | 50 | 6 | 54.76 | 2.9844 | 2022-02-23 11:45 | 10.9 | 7.9156 | 10.355 | 7.3706 | 2 | PowerSafe | 2DDm50-13 | 5.2272 | 2.2428 | 2 | 40 | 30 | 27.0156 | 67 |  | 0 | 7.9156 | 7.3706 | 72.62 | 71.1789 | 2.2428 | 42.906 | 30 | 2.9844 | 27.0156 | 0 | 27.0156 | 90.0519 |  | Single | 2DDm50-13 | 0 | 0 | 0 | 0 | 0 | 2DDm50-13
DNDN71; SYS 01 | SCOTLAND | DUNDEE | Redstream Optical Network Site | DNDN71 | Eaton Powerware APR48-ES | 36.6 | 17 | 157 | 8.5565 | 2024-05-02 | 25.5322 | 16.9757 | 18.9442 | 10.3877 | 4 | PowerSafe | 2DDm85-15 | 20.2176 | 11.6611 | 3 | 30 | 22.5 | 13.9435 | 17 |  | 4.7 | 12.2757 | 5.6877 | 48.0792 | 30.0234 | 6.9611 | 34.4309 | 22.5 | 8.5565 | 13.9435 | 4.7 | 9.2435 | 41.0822 |  | Single | 2DDm85-15 | 0 | RA | 0 | 0 | 0 | 2DDm85-15
DNDTC1;DCSYS01 | SCOTLAND | DUNDEE | GIS Migrated - Capped | DNDTC1 | Eaton Powerware APR48-ES | 36.6 | 6 | 76 | 4.142 | 2024-05-02 | 7.9788 | 3.8368 | 5.7552 | 1.6132 | 6 | Enersys | 12V155F | 8.424 | 4.282 | 2 | 10 | 7.5 | 3.358 | 0 | Space | 0 | 3.8368 | 1.6132 | 48.0874 | 28.0303 | 4.282 | 50.831 | 7.5 | 4.142 | 3.358 | 0 | 3.358 | 44.7733 | Capped | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
DNFNP1; DC SYS01 | SCOTLAND | DUNFERMLINE | GIS Migrated - Capped | DNFNP1 | Eaton Powerware APR48-ES | 36.6 | 6 | 46 | 2.507 | 2024-05-02 | 7.9788 | 5.4718 | 6.7035 | 4.1965 | 6 | PowerSafe | 12V101F (4 hour Rate) | 5.3784 | 2.8714 | 2 | 6.7 | 5.025 | 2.518 | 2 | Space | 0.5 | 4.9718 | 3.6965 | 62.3126 | 55.1428 | 2.3714 | 44.0912 | 5.025 | 2.507 | 2.518 | 0.5 | 2.018 | 40.1592 | Capped | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
DONTN1;DC SYS01 | NORTH EAST | DONCASTER | GIS Migrated - Capped | DONTN1 | Duvine DD686 | 75 | 7 | 180 | 9.81 | 2022-02-10 09:30 | 19.62 | 9.81 | 11.445 | 1.635 | 2 | PowerSafe | DDm100-25 | 21.1248 | 11.3148 | 3 | 26 | 19.5 | 9.69 | 4 | Space | 0 | 9.81 | 1.635 | 50 | 14.2857 | 11.3148 | 53.5617 | 19.5 | 9.81 | 9.69 | 0 | 9.69 | 49.6923 | Capped | Single | DDm100-25 | 0 | 0 | 0 | 0 | 0 | DDm100-25
DVSTB1; DC SYS01 | SOUTH WEST | DEVIZES | Redstream Optical Network Site | DVSTB1 | Eaton Powerware APR48-ES | 36.6 | 6 | 10 | 0.545 | 2021-12-23 12:00 | 7.9788 | 7.4338 | 3.7605 | 3.2155 | 6 | Enersys | 12V190F | 11.1845 | 10.6395 | 2 | 10 | 7.5 | 6.955 | 14 |  | 0 | 7.4338 | 3.2155 | 93.1694 | 85.5072 | 10.6395 | 95.1272 | 7.5 | 0.545 | 6.955 | 0 | 6.955 | 92.7333 |  | Single | 12V190F | 0 | 0 | 0 | 0 | 0 | 12V190F
DWLTM1;DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | MOUNT EAGLE | Capped | DWLTM1 | Eltek FLATPACK2-1800 | 37.5 | 4 | 36 | 1.962 | 2021-10-11 12:07 | 4.905 | 2.943 | 5.8042 | 3.8422 | 6 | Enersys | SBS C11F | 5.184 | 3.222 | 0 | 0 | 0 | -1.962 | 0 | Space; Air Con | 4 | -1.057 | -0.15775 | -21.5494 | -2.7178 | -0.778 | -15.0077 | 0 | 1.962 | -1.962 | 4 | -5.962 | #DIV/0! | Capped | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
ECBTC1; DC SYS01 | NORTH EAST | ECCLES | Redstream Optical Network Site | EBCTC1 | Power One PMP 10.48 SIC | 22 | 4 | 20 | 1.09 | 2022-11-14 | 2.8776 | 1.7876 | 2.289 | 1.199 | 3 | Enersys | 12V100F | 2.929 | 1.839 | 2 | 4.5 | 3.375 | 2.285 | 3 |  | 1 | 0.7876 | 0.199 | 27.37 | 8.6938 | 0.83896 | 28.6436 | 3.375 | 1.09 | 2.285 | 1 | 1.285 | 38.0741 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
EDBCD1;DC SYS01 | SCOTLAND | EDINBURGH | Redstream Optical Network Site | EDBN07 | Duvine DD686 | 75 | 6 | 244 | 13.298 | 2021-08-23 12:00 | 16.35 | 3.052 | 11.1725 | -2.1255 | 2 | PowerSafe | DDm85-21 | 14.4288 | 1.1308 | 2 | 10 | 7.5 | -5.798 | 0 |  | 0 | 3.052 | -2.1255 | 18.6667 | -19.0244 | 1.1308 | 7.8371 | 7.5 | 13.298 | -5.798 | 0 | -5.798 | -77.3067 |  | Single | DDm85-21 | 0 | 0 | 0 | 0 | 0 | DDm85-21
EDBTG1;DC SYSA | SCOTLAND | EDINBURGH | Capped | EDBTG1 | Eaton Powerware APR48-ES | 36.6 | 50 | 437 | 23.8165 | 2024-05-03 | 78.1922 | 54.3757 | 54.1403 | 30.3238 | 4 | PowerSafe | DDm125-33 | 71.1072 | 47.2907 | 9 | 140 | 105 | 81.1835 | 4 | Power | 22.55 | 31.8257 | 7.7738 | 40.7019 | 14.3586 | 24.7407 | 34.7935 | 105 | 23.8165 | 81.1835 | 22.55 | 58.6335 | 55.8414 | Capped | Dual | DDm125-33 | 0 | RA | PX | 0 | OPEX | DDm125-33
EDBTG1;DC SYSB | SCOTLAND | EDINBURGH | Capped | EDBTG1 | Eaton Powerware APR48-ES | 36.6 | 50 | 503 | 27.4135 | 2024-05-03 | 78.1922 | 50.7787 | 54.1403 | 26.7268 | 4 | PowerSafe | DDm125-33 | 71.1072 | 43.6937 | 9 | 140 | 105 | 77.5865 | 4 | Power | 22.05 | 28.7287 | 4.6768 | 36.7412 | 8.6383 | 21.6437 | 30.4381 | 105 | 27.4135 | 77.5865 | 22.05 | 55.5365 | 52.8919 | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | SCOTLAND | EDINBURGH | GIS Migrated - Capped | EDBTN1 | Eaton Powerware APR48-ES | 36.6 | 42 | 447 | 24.3615 | 2024-05-03 | 65.4262 | 41.0647 | 55.2139 | 30.8525 | 3 | PowerSafe | DDm125-27 | 43.2864 | 18.9249 | 4 | 90 | 67.5 | 43.1385 | 31 | Power | 7.7515 | 33.3132 | 23.101 | 50.9172 | 41.839 | 11.1734 | 25.8127 | 67.5 | 63.002 | 4.498 | 15.503 | -11.005 | -16.3037 | Capped | Dual | DDm125-27 | P-Core | 0 | 0 | 0 | 0 | DDm125-27
EDBTN1;DC SYSB | SCOTLAND | EDINBURGH | GIS Migrated - Capped | EDBTN1 | Eaton Powerware APR48-ES | 36.6 | 42 | 709 | 38.6405 | 2024-05-03 | 65.4262 | 26.7857 | 55.2139 | 16.5735 | 3 | PowerSafe | DDm125-27 | 43.2864 | 4.6459 | 4 | 90 | 67.5 | 28.8595 | 31 | Power | 7.7515 | 19.0342 | 8.822 | 29.0926 | 15.9778 | -3.1056 | -7.1745 | [6 empty] | Capped | Dual | DDm125-27 | 0 | 0 | 0 | 0 | 0 | DDm125-27
EGNTM1;DC SYS01 | SCOTLAND | ELGIN | Redstream Optical Network Site | EGNTM1 | Eltek FLATPACK2-1800 | 37.5 | 4 | 48 | 2.616 | 2022-01-03 08:10 | 4.905 | 2.289 | 5.8042 | 3.1883 | 6 | Enersys | SBS C11F | 5.184 | 2.568 | 2 | 6.7 | 5.025 | 2.409 | 3 |  | 1 | 1.289 | 2.1883 | 26.2793 | 37.7008 | 1.568 | 30.2469 | 5.025 | 2.616 | 2.409 | 1 | 1.409 | 28.0398 |  | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
EVMN01;DC SYS01 | MIDLANDS | EVESHAM | Redstream Optical Network Site | EVMN01 | Eaton Powerware APR48-ES | 36.6 | 9 | 49 | 2.6705 | 2024-05-03 | 12.7661 | 10.0956 | 9.4721 | 6.8016 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 7.4383 | 2 | 15 | 11.25 | 8.5795 | 19 |  | 1 | 9.0956 | 5.8016 | 71.248 | 61.2494 | 6.4383 | 63.6901 | 11.25 | 2.6705 | 8.5795 | 1 | 7.5795 | 67.3733 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
EXR;DC SYS01 | SOUTH WEST | EXETER | Redstream Optical Network Site | EXR | Eaton Powerware APR48-ES | 36.6 | 18 | 200 | 10.9 | 2021-08-11 12:00 | 27.1279 | 16.2279 | 19.0859 | 8.1859 | 2 | PowerSafe | DDm85-33 | 22.9824 | 12.0824 | 5 | 67 | 50.25 | 39.35 | 71 |  | 3 | 13.2279 | 5.1859 | 48.7613 | 27.1714 | 9.0824 | 39.5189 | 50.25 | 10.9 | 39.35 | 3 | 36.35 | 72.3383 |  | Single | DDm85-33 | 0 | 0 | 0 | 0 | 0 | DDm85-33
EXRN03-DCSYSa | SOUTH WEST | EXETER | Redstream Optical Network Site | EXR | Eaton Powerware APR48-ES | 36.6 | 16 | 13 | 0.7085 | 2023-05-02 | 23.9364 | 23.2279 | 18.8025 | 18.094 | 2 | PowerSafe | DDm85-25 | 17.4096 | 16.7011 | 5 | 67 | 50.25 | 49.5415 | 71 |  | 5.9 | 17.3279 | 12.194 | 72.3914 | 64.8531 | 10.8011 | 62.0411 | 50.25 | 1.308 | 48.942 | 11.7 | 37.242 | 74.1134 |  | Dual | DDm85-25 | 0 | 0 | 0 | AM | 0 | DDm85-25
EXRN03-DCSYSb | SOUTH WEST | EXETER | Redstream Optical Network Site | EXR | Eaton Powerware APR48-ES | 36.6 | 16 | 11 | 0.5995 | 2023-05-02 | 23.9364 | 23.3369 | 18.8025 | 18.203 | 2 | PowerSafe | DDm85-25 | 17.4096 | 16.8101 | 5 | 67 | 50.25 | 49.6505 | 71 |  | 5.8 | 17.5369 | 12.403 | 73.2646 | 65.9646 | 11.0101 | 63.2415 | [7 empty] | Dual | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
FKE;DC SYS01 | SOUTH EAST | FOLKESTONE | Redstream Optical Network Site | FKE | Eaton Powerware APR48-ES | 36.6 | 20 | 145 | 7.9025 | 2021-03-31 09:00 | 30.3194 | 22.4169 | 21.5493 | 13.6468 | 2 | PowerSafe | DDm125-25 | 26.6544 | 18.7519 | 3 | 30 | 22.5 | 14.5975 | 19 |  | 0 | 22.4169 | 13.6468 | 73.9359 | 63.3283 | 18.7519 | 70.352 | 22.5 | 7.9025 | 14.5975 | 0 | 14.5975 | 64.8778 |  | Single | DDm125-25 | 0 | 0 | 0 | 0 | 0 | DDm125-25
FLNTT1;DC SYS01 | NORTH EAST | MORPETH | GIS Migrated | FLNTT1 | Power One PMP 10.48 SIC | 22 | 6 | 13 | 0.7085 | 2022-05-19 09:30 | 4.796 | 4.0875 | 3.815 | 3.1065 | 4 | PowerSafe | SBS 12V100F | 3.767 | 3.0585 | 2 | 6.7 | 5.025 | 4.3165 | 6 |  | 0 | 4.0875 | 3.1065 | 85.2273 | 81.4286 | 3.0585 | 81.1921 | 5.025 | 0.7085 | 4.3165 | 0 | 4.3165 | 85.9005 |  | Single | SBS 12V100F | 0 | 0 | 0 | 0 | 0 | SBS 12V100F
FMYN31; DC SYS01 | THAMES VALLEY | FRIMLEY | GIS Migrated | FMYN31 | Eaton Powerware APR48-ES | 36.6 | 7 | 52 | 2.834 | 2024-05-03 | 9.5746 | 6.7406 | 8.4802 | 5.6462 | 8 | Enersys | 12V100F | 7.8106 | 4.9766 | 2 | 15 | 11.25 | 8.416 | 21 |  | 0 | 6.7406 | 5.6462 | 70.4007 | 66.581 | 4.9766 | 63.7158 | 11.25 | 2.834 | 8.416 | 0 | 8.416 | 74.8089 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
FRNN03-DCSYS01a | SOUTH WEST | FRADDON | Redstream Optical Network Site | FRNN03 | Eaton Powerware APR48-ES | 36.6 | 18 | 23 | 1.2535 | 2024-05-03 | 27.1279 | 25.8744 | 22.7919 | 21.5384 | 2 | PowerSafe | DDm85-25 | 17.4096 | 16.1561 | 6 | 150 | 112.5 | 111.2465 | 22 |  | 5.9 | 19.9744 | 15.6384 | 73.6305 | 68.6138 | 10.2561 | 58.9106 | 112.5 | 3.1065 | 109.3935 | 11.7 | 97.6935 | 86.8387 |  | Dual | DDm85-25 | 0 | 0 | 0 | AM | 0 | DDm85-25
FRNN03-DCSYS01b | SOUTH WEST | FRADDON | Redstream Optical Network Site | FRNN03 | Eaton Powerware APR48-ES | 36.6 | 18 | 34 | 1.853 | 2024-05-03 | 27.1279 | 25.2749 | 22.7919 | 20.9389 | 2 | PowerSafe | DDm85-25 | 17.4096 | 15.5566 | 6 | 150 | 112.5 | 110.647 | 22 |  | 5.8 | 19.4749 | 15.1389 | 71.7892 | 66.4223 | 9.7566 | 56.0415 | [7 empty] | Dual | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
GCRTB1;DC SYS01 | SOUTH WEST | GLOUCESTER | GIS MIGRATING | GCRTB1 | Eaton Powerware APR48-ES | 36.6 | 23 | 279 | 15.2055 | 2024-05-03 | 35.1067 | 19.9012 | 22.0834 | 6.8779 | 2 | PowerSafe | DDm125-33 | 35.5536 | 20.3481 | 3 | 60 | 45 | 29.7945 | 24 |  | 3.9 | 16.0012 | 2.9779 | 45.5788 | 13.4848 | 16.4481 | 46.2628 | 45 | 15.2055 | 29.7945 | 3.9 | 25.8945 | 57.5433 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
GFDCD1;DC SYS01A | SOUTH | GUILDFORD | Redstream Optical Network Site | GFDCD1 | Eaton Powerware APR48-ES | 36.6 | 42 | 327 | 17.8215 | 2024-05-03 | 65.4262 | 47.6047 | 49.0827 | 31.2612 | 3 | PowerSafe | DDm125-33 | 53.3304 | 35.5089 | 5 | 240 | 180 | 162.1785 | 60 |  | 7.3 | 40.3047 | 23.9612 | 61.6033 | 48.818 | 28.2089 | 52.8946 | 180 | 40.984 | 139.016 | 13.9 | 125.116 | 69.5089 |  | Dual | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
GFDCD1;DC SYS01B | SOUTH | GUILDFORD | Redstream Optical Network Site | GFDCD1 | Eaton Powerware APR48-ES | 36.6 | 42 | 425 | 23.1625 | 2024-05-03 | 65.4262 | 42.2637 | 49.0827 | 25.9202 | 3 | PowerSafe | DDm125-33 | 53.3304 | 30.1679 | 5 | 240 | 180 | 156.8375 | 60 |  | 6.6 | 35.6637 | 19.3202 | 54.5098 | 39.3625 | 23.5679 | 44.1922 | [7 empty] | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
GLWN07;DC SYS A | SCOTLAND | GLASGOW | GIS Migrated - Capped | GLWN07 | Eaton Powerware APR48-ES | 36.6 | 54 | 865 | 47.1425 | 2024-05-03 | 84.5753 | 37.4328 | 62.1191 | 14.9766 | 4 | PowerSafe | DDm125-33 | 71.1072 | 23.9647 | 4 | 120 | 90 | 42.8575 | 51 | Power | 11.75 | 25.6828 | 3.2266 | 30.3668 | 5.1942 | 12.2147 | 17.1779 | 90 | 79.57 | 10.43 | 25.7 | -15.27 | -16.9667 | Capped | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
GLWN07;DC SYS B | SCOTLAND | GLASGOW | GIS Migrated - Capped | GLWN07 | Eaton Powerware APR48-ES | 36.6 | 54 | 595 | 32.4275 | 2024-05-03 | 84.5753 | 52.1478 | 62.1191 | 29.6916 | 4 | PowerSafe | DDm125-33 | 71.1072 | 38.6797 | 4 | 120 | 90 | 57.5725 | 51 | Power | 13.95 | 38.1978 | 15.7416 | 45.1642 | 25.341 | 24.7297 | 34.7781 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
GLWTO1;DC SYS01 | SCOTLAND | GLASGOW | Redstream Optical Network Site | GLWTO1 | Eaton Powerware APR48-ES | 36.6 | 19 | 181 | 9.8645 | 2024-05-03 | 28.7237 | 18.8592 | 19.5546 | 9.6901 | 2 | PowerSafe | DDm125-25 | 26.6544 | 16.7899 | 3 | 30 | 22.5 | 12.6355 | 61 |  | 4.4 | 14.4592 | 5.2901 | 50.3389 | 27.053 | 12.3899 | 46.4835 | 22.5 | 9.8645 | 12.6355 | 4.4 | 8.2355 | 36.6022 |  | Single | DDm125-25 | 0 | RA | 0 | 0 | 0 | DDm125-25
GLWTW1;DC SYS01 | SCOTLAND | GLASGOW | Redstream Optical Network Site | GLWTW1 | Eaton Powerware APR48-ES | 36.6 | 35 | 593 | 32.3185 | 2024-05-03 | 54.2558 | 21.9373 | 35.1198 | 2.8013 | 3 | PowerSafe | DDm125-33 | 53.3304 | 21.0119 | 5 | 84 | 63 | 30.6815 | 3 |  | 3 | 18.9373 | -0.1987 | 34.9038 | -0.56578 | 18.0119 | 33.7742 | 63 | 32.3185 | 30.6815 | 3 | 27.6815 | 43.9389 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
GRSTB1;DC SYS01 | SCOTLAND | GLENROTHES | Redstream Optical Network Site | GRSTB1 | Eaton Powerware APR48-ES | 36.6 | 3 | 9 | 0.4905 | 2024-05-03 | 3.1915 | 2.701 | 2.8994 | 2.4089 | 2 | PowerSafe | 12V101F (4 hour Rate) | 1.7928 | 1.3023 | 2 | 6.7 | 5.025 | 4.5345 | 6 |  | 2.7 | 0.00102 | -0.2911 | 0.03196 | -10.04 | -1.3977 | -77.9618 | 5.025 | 0.4905 | 4.5345 | 2.7 | 1.8345 | 36.5075 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
GWK;DC SYS01 | SOUTH EAST | CRAWLEY | Capped | GWK | Eaton Powerware APR48 - 3G | 37.5 | 8 | 150 | 8.175 | 2024-05-03 | 11.445 | 3.27 | 10.0879 | 1.9129 | 6 | Enersys | 12V155F | 8.424 | 0.249 | 3 | 16 | 12 | 3.825 | 3 | Space | 0.5 | 2.77 | 1.4129 | 24.2027 | 14.0063 | -0.251 | -2.9796 | 12 | 8.175 | 3.825 | 0.5 | 3.325 | 27.7083 | Capped | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
HHD;DC SYS01 | NORTHERN HOME COUNTIES | HEMEL HEMPSTEAD | Redstream Optical Network Site | HHD | Eaton Powerware APR48-ES | 36.6 | 19 | 252 | 13.734 | 2023-07-04 | 28.7237 | 14.9897 | 17.8378 | 4.1039 | 3 | PowerSafe | DDm85-27 | 28.188 | 14.454 | 6 | 30 | 22.5 | 8.766 | 16 |  | 2 | 12.9897 | 2.1039 | 45.2229 | 11.7943 | 12.454 | 44.1819 | 22.5 | 13.734 | 8.766 | 2 | 6.766 | 30.0711 |  | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
HLDA11;DC SYS01 | LONDON | HILLINGDON | Redstream Optical Network Site | HLDA11 | Eaton Powerware APR48-ES | 36.6 | 8 | 108 | 5.886 | 2024-05-03 | 11.1703 | 5.2843 | 6.9869 | 1.1009 | 16 | Enersys | 12V100F | 15.6211 | 9.7351 | 2 | 65 | 48.75 | 42.864 | 12 |  | 0 | 5.2843 | 1.1009 | 47.3068 | 15.7566 | 9.7351 | 62.3202 | 48.75 | 5.886 | 42.864 | 0 | 42.864 | 87.9262 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
HLDA12;DC SYS01 | LONDON | HILLINGDON | Redstream Optical Network Site | HLDA12 | Eaton Powerware APR48-ES | 36.6 | 8 | 112 | 6.104 | 2024-05-03 | 11.1703 | 5.0663 | 6.9869 | 0.8829 | 16 | Enersys | 12V100F | 15.6211 | 9.5171 | 2 | 65 | 48.75 | 42.646 | 4 |  | 0 | 5.0663 | 0.8829 | 45.3552 | 12.6365 | 9.5171 | 60.9247 | 48.75 | 6.104 | 42.646 | 0 | 42.646 | 87.479 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
HLWN02;DC SYS01 | ANGLIA | HARLOW | Redstream Optical Network Site | HLWN02 | Eaton Powerware APR48-ES | 36.6 | 17 | 199 | 10.8455 | 2022-11-15 | 25.5322 | 14.6867 | 22.6502 | 11.8047 | 2 | PowerSafe | DDm85-21 | 14.4288 | 3.5833 | 4 | 90 | 67.5 | 56.6545 | 38 |  | 1 | 13.6867 | 10.8047 | 53.6056 | 47.7024 | 2.5833 | 17.9038 | 67.5 | 10.8455 | 56.6545 | 1 | 55.6545 | 82.4511 |  | Single | DDm85-21 | 0 | 0 | 0 | 0 | 0 | DDm85-21
HRWN02;DC SYS01 | LONDON | HOUNSLOW | GIS Migrated | HRWN02 | Eaton Powerware APR48-ES | 36.6 | 41 | 650 | 35.425 | 2020-08-19 | 63.8304 | 28.4054 | 47.088 | 11.663 | 3 | PowerSafe | DDm125-33 | 53.3304 | 17.9054 | 4 | 90 | 67.5 | 32.075 | 235 |  | 5.9 | 22.5054 | 5.763 | 35.2581 | 12.2388 | 12.0054 | 22.5114 | 67.5 | 35.425 | 32.075 | 5.9 | 26.175 | 38.7778 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
HTE;DC SYS01 | NORTH EAST | HARROGATE | Redstream Optical Network Site | HTE | Duvine DD686 | 75 | 5 | 90 | 4.905 | 2022-04-01 13:00 | 13.08 | 8.175 | 9.8645 | 4.9595 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 5.2038 | 2 | 12 | 9 | 4.095 | 4 |  | 1 | 7.175 | 3.9595 | 54.8547 | 40.1389 | 4.2038 | 41.5855 | 9 | 4.905 | 4.095 | 1 | 3.095 | 34.3889 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
IGNN01;DC SYS01 | LONDON | LONDON | GIS Migrated - Capped | IGNN01 | Eaton Powerware APR48-ES | 36.6 | 26 | 649 | 35.3705 | 2024-05-03 | 39.894 | 4.5235 | 28.0675 | -7.303 | 2 | PowerSafe | DDm125-33 | 35.5536 | 0.1831 | 3 | 98 | 73.5 | 38.1295 | 119 | DC Power | 4.4 | 0.1235 | -11.703 | 0.30957 | -41.6959 | -4.2169 | -11.8607 | 73.5 | 35.3705 | 38.1295 | 4.4 | 33.7295 | 45.8905 | Capped | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
INVN41;DC SYS01 | SCOTLAND | INVERNESS | GIS Migrated | INVN41 | Eaton Powerware APR48-ES | 36.6 | 9 | 138 | 7.521 | 2024-05-03 | 12.7661 | 5.2451 | 9.4721 | 1.9511 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 2.5878 | 2 | 15 | 11.25 | 3.729 | 29 |  | 6.4 | -1.1549 | -4.4489 | -9.0468 | -46.9685 | -3.8122 | -37.7117 | 11.25 | 7.521 | 3.729 | 6.4 | -2.671 | -23.7422 |  | Single | 2DDm85-15 | 0 | RA | 0 | 0 | 0 | 2DDm85-15
INVTL1;DC SYS01 | SCOTLAND | INVERNESS | Capped | INVTL1 | Eaton Powerware APR48-ES | 36.6 | 9 | 118 | 6.431 | 2024-05-03 | 12.7661 | 6.3351 | 10.3332 | 3.9022 | 8 | Enersys | 12V155F | 11.232 | 4.801 | 2 | 14 | 10.5 | 4.069 | 1 | Planned closure | 4 | 2.3351 | -0.0978 | 18.2913 | -0.94647 | 0.801 | 7.1314 | 10.5 | 6.431 | 4.069 | 4 | 0.069 | 0.65714 | Capped | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
IODN01;DC SYS01 | LONDON | LONDON | GIS Migrated | IODN01 | Eaton Powerware NPR.48 | 55 | 20 | 433 | 23.5985 | 2021-06-22 | 45.562 | 21.9635 | 35.1525 | 11.554 | 2 | PowerSafe | DDm125-33 | 35.5536 | 11.9551 | 3 | 200 | 150 | 126.4015 | 16 |  | 10.4 | 11.5635 | 1.154 | 25.3797 | 3.2828 | 1.5551 | 4.374 | 150 | 23.5985 | 126.4015 | 10.4 | 116.0015 | 77.3343 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | OPEX | DDm125-33
IODTA1;DC SYS01 | LONDON | LONDON | Redstream Optical Network Site | IODTA1 | Eaton Powerware APR48-ES | 36.6 | 32 | 526 | 28.667 | 2024-05-03 | 49.4686 | 20.8016 | 31.2612 | 2.5942 | 3 | PowerSafe | SBS EON 1800 | 49.248 | 20.581 | 4 | 81 | 60.75 | 32.083 | 3 |  | 1 | 19.8016 | 1.5942 | 40.0286 | 5.0996 | 19.581 | 39.76 | 60.75 | 28.667 | 32.083 | 1 | 31.083 | 51.1654 |  | Single | SBS EON 1800 |  |  |  |  | OPEX | SBS EON 1800
IPWTN1;DC SYS01 | ANGLIA | IPSWICH | GIS Migrated | IPWTN1 | Eaton Powerware APR48-ES | 36.6 | 26 | 285 | 15.5325 | 2022-10-20 | 39.894 | 24.3615 | 28.0675 | 12.535 | 2 | PowerSafe | DDm125-33 | 35.5536 | 20.0211 | 3 | 30 | 22.5 | 6.9675 | 98 |  | 6.7 | 17.6615 | 5.835 | 44.2711 | 20.7892 | 13.3211 | 37.4677 | 22.5 | 15.5325 | 6.9675 | 6.7 | 0.2675 | 1.1889 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
IVER02; DC SYS01 | THAMES VALLEY | IVER | GIS Migrated - Capped | IVER02 | Eaton Powerware APR48-ES | 36.6 | 5 | 99 | 5.3955 | 2021-07-06 14:00 | 6.383 | 0.98754 | 4.7088 | -0.6867 | 6 | PowerSafe | 12V101F (2 Hour rate) | 9.2146 | 3.8191 | 1 | 12 | 9 | 3.6045 | 4 | Space; Power; Autonomy | 0 | 0.98754 | -0.6867 | 15.4713 | -14.5833 | 3.8191 | 41.4459 | 9 | 5.3955 | 3.6045 | 0 | 3.6045 | 40.05 | Capped | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
KLNN01;DC SYS01 | ANGLIA | KINGS LYNN | GIS Migrated - Capped | KLNN01 | Duvine DD686 | 75 | 3 | 16 | 0.872 | 2021-08-05 17:00 | 6.54 | 5.668 | 7.2267 | 6.3547 | 2 | Enersys | 12V105F | 1.7928 | 0.9208 | 2 | 5 | 3.75 | 2.878 | 1 | Space; Power; Air Con | 0 | 5.668 | 6.3547 | 86.6667 | 87.9336 | 0.9208 | 51.361 | 3.75 | 0.872 | 2.878 | 0 | 2.878 | 76.7467 | Capped | Single | 12V105F | 0 | 0 | 0 | 0 | 0 | 12V105F
KNLTS1;DC SYS01 | NORTH WEST | KENDAL | Redstream Optical Network Site | KNLTS1 | Eaton Powerware APR48-ES | 36.6 | 9 | 125 | 6.8125 | 2024-05-03 | 12.7661 | 5.9536 | 9.4721 | 2.6596 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 3.2963 | 2 | 30 | 22.5 | 15.6875 | 4 |  | 0.5 | 5.4536 | 2.1596 | 42.7193 | 22.7996 | 2.7963 | 27.662 | 22.5 | 6.8125 | 15.6875 | 0.5 | 15.1875 | 67.5 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
LCT;DC SYS01 | MIDLANDS | LEICESTER | Redstream Optical Network Site | LCT | Eaton Powerware APR48-ES | 36.6 | 70 | 932 | 50.794 | 2024-05-03 | 110.1074 | 59.3134 | 76.5943 | 25.8003 | 4 | PowerSafe | 2CP3000 | 95.6102 | 44.8162 | 3 | 80 | 60 | 9.206 | 11 |  | 13.5 | 45.8134 | 12.3003 | 41.6079 | 16.059 | 31.3162 | 32.7541 | 82.5 | 50.794 | 31.706 | 13.5 | 18.206 | 22.0679 |  | Single | 2CP3000 | 0 | RA | 0 | 0 | 0 | 2CP3000
LDMS13;DC SYS01 A | NORTH EAST | LEEDS | CLOSED | LDMS13 | Eaton Powerware NPR.48 | 55 | 8 | 45 | 2.4525 | 2022-06-01 13:00 | 16.786 | 14.3335 | 17.7125 | 15.26 | 6 | PowerSafe | 12V101F (4 hour Rate) | 5.3784 | 2.9259 | 1 | 32 | 24 | 21.5475 | 4 |  | 0 | 14.3335 | 15.26 | 85.3896 | 86.1538 | 2.9259 | 54.4009 | 24 | 7.0305 | 16.9695 | 0 | 16.9695 | 70.7062 |  | Dual | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
LDMS13;DC SYS01 B | NORTH EAST | LEEDS | CLOSED | LDMS13 | Eaton Powerware NPR.48 | 55 | 8 | 84 | 4.578 | 2022-05-19 15:30 | 16.786 | 12.208 | 17.7125 | 13.1345 | 6 | PowerSafe | 12V101F (4 hour Rate) | 5.3784 | 0.8004 | 1 | 32 | 24 | 19.422 | 4 |  | 0 | 12.208 | 13.1345 | 72.7273 | 74.1538 | 0.8004 | 14.8817 | [7 empty] | Dual | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
LDSCD2;DC SYS A | NORTH EAST | LEEDS | GIS Migrated | LDSCD2 | Eaton Powerware NPR.48 | 55 | 69 | 1632 | 88.944 | 2024-05-03 | 163.064 | 74.12 | 138.43 | 49.486 | 6 | PowerSafe | DDm125-33 | 106.6608 | 17.7168 | 7 | 260 | 195 | 106.056 | 37 |  | 17.5 | 56.62 | 31.986 | 34.7226 | 23.1063 | 0.2168 | 0.20326 | 195 | 137.449 | 57.551 | 38.2 | 19.351 | 9.9236 |  | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
LDSCD2;DC SYS B | NORTH EAST | LEEDS | GIS Migrated | LDSCD2 | Eaton Powerware NPR.48 | 55 | 70 | 890 | 48.505 | 2024-05-03 | 165.462 | 116.957 | 141.4275 | 92.9225 | 6 | PowerSafe | DDm125-33 | 106.6608 | 58.1558 | 7 | 260 | 195 | 146.495 | 37 |  | 20.7 | 96.257 | 72.2225 | 58.1747 | 51.0668 | 37.4558 | 35.1167 | [7 empty] | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
LDSN14; DC SYS01 | NORTH EAST | LEEDS | Redstream Optical Network Site | LDSN14 | Eaton Powerware APR48 - 3G | 37.5 | 12 | 120 | 6.54 | 2022-03-17 16:00 | 17.985 | 11.445 | 10.4367 | 3.8967 | 2 | PowerSafe | DDm85-27 | 18.792 | 12.252 | 2 | 32 | 24 | 17.46 | 3 |  | 0.1 | 11.345 | 3.7967 | 63.0803 | 36.3787 | 12.152 | 64.6658 | 24 | 6.54 | 17.46 | 0.1 | 17.36 | 72.3333 |  | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
LDSTS1;DC SYS01 | NORTH EAST | LEEDS | Redstream Optical Network Site | LDSTS1 | Eaton Powerware APR48-ES | 36.6 | 35 | 462 | 25.179 | 2024-05-03 | 54.2558 | 29.0768 | 35.1198 | 9.9408 | 3 | PowerSafe | DDm125-33 | 53.3304 | 28.1514 | 7 | 180 | 135 | 109.821 | 135 |  | 8.1 | 20.9768 | 1.8408 | 38.6628 | 5.2415 | 20.0514 | 37.5984 | 135 | 25.179 | 109.821 | 8.1 | 101.721 | 75.3489 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
LIVN01;DC SYS01 | SCOTLAND | LIVINGSTON | Redstream Optical Network Site | LIVN01 | Eaton Powerware APR48-ES | 36.6 | 35 | 523 | 28.5035 | 2024-05-03 | 54.2558 | 25.7523 | 35.1198 | 6.6163 | 3 | PowerSafe | DDm125-33 | 53.3304 | 24.8269 | 4 | 90 | 67.5 | 38.9965 | 44 |  | 2 | 23.7523 | 4.6163 | 43.7784 | 13.1444 | 22.8269 | 42.8028 | 67.5 | 28.5035 | 38.9965 | 2 | 36.9965 | 54.8096 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
LLDTE1;DC SYS01 | NORTH WEST | PRESTON | GIS Migrated | LLDTE1 | Eaton Powerware APR48-ES | 36.6 | 18 | 185 | 10.0825 | 2024-05-03 | 27.1279 | 17.0454 | 12.1099 | 2.0274 | 2 | PowerSafe | DDm125-33 | 35.5536 | 25.4711 | 2 | 30 | 22.5 | 12.4175 | 174 |  | 5.9 | 11.1454 | -3.8726 | 41.0847 | -31.9788 | 19.5711 | 55.0467 | 22.5 | 10.0825 | 12.4175 | 5.9 | 6.5175 | 28.9667 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
LMSCN2;DC SYS01 | MIDLANDS | LEAMINGTON SPA | Capped | LMSCN2 | Eaton Powerware APR48-ES | 36.6 | 11 | 142 | 7.739 | 2022-05-26 14:30 | 15.9576 | 8.2186 | 6.0495 | -1.6895 | 3 | PowerSafe | DDm85-21 | 21.6432 | 13.9042 | 3 | 28 | 21 | 13.261 | 1 | Space | 0 | 8.2186 | -1.6895 | 51.5027 | -27.9279 | 13.9042 | 64.2428 | 21 | 7.739 | 13.261 | 0 | 13.261 | 63.1476 | Capped | Single | DDm85-21 | 0 | 0 | 0 | 0 | 0 | DDm85-21
LPLTB1;DC SYS01 | NORTH WEST | PRESCOT | Redstream Optical Network Site | LPLTB1 | Eaton Powerware APR48-ES | 36.6 | 10 | 99 | 5.3955 | 2024-05-03 | 14.3618 | 8.9663 | 17.7343 | 12.3388 | 4 | Enersys | SBS C11F | 3.456 | -1.9395 | 2 | 15 | 11.25 | 5.8545 | 4 |  | 0 | 8.9663 | 12.3388 | 62.4317 | 69.5759 | -1.9395 | -56.1198 | 11.25 | 5.3955 | 5.8545 | 0 | 5.8545 | 52.04 |  | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
LPLTK1;DC SYS01 | NORTH WEST | LIVERPOOL | GIS Migrated | LPLTK1 | Eaton Powerware APR48-ES | 36.6 | 26 | 319 | 17.3855 | 2024-05-03 | 39.894 | 22.5085 | 28.0675 | 10.682 | 2 | PowerSafe | DDm125-33 | 35.5536 | 18.1681 | 3 | 50 | 37.5 | 20.1145 | 18 |  | 1.7 | 20.8085 | 8.982 | 52.1595 | 32.0014 | 16.4681 | 46.3191 | 37.5 | 17.3855 | 20.1145 | 1.7 | 18.4145 | 49.1053 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
LSWN01;DC SYS01 | LONDON | LONDON | Capped | LSWN01 | Duvine DD686 | 75 | 35 | 1430 | 77.935 | 2023-01-18 | 111.18 | 33.245 | 95.375 | 17.44 | 4 | PowerSafe | DDm125-33 (2hr rate) | 113.616 | 35.681 | 1 | 95 | 71.25 | -6.685 | 45 | Power; Autonomy | 11.5 | 21.745 | 5.94 | 19.5584 | 6.228 | 24.181 | 21.2831 | 71.25 | 77.935 | -6.685 | 11.5 | -18.185 | -25.5228 | Capped | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
LTNDN1;DC SYS01 | NORTHERN HOME COUNTIES | LUTON | Capped | LTNDN1 | Duvine DD686 | 75 | 12 | 240 | 13.08 | 2022-04-25 17:00 | 35.97 | 22.89 | 27.5225 | 14.4425 | 2 | PowerSafe | DDm100-33 | 28.1232 | 15.0432 | 2 | 30 | 22.5 | 9.42 | 7 | Space | 1 | 21.89 | 13.4425 | 60.8563 | 48.8419 | 14.0432 | 49.9346 | 22.5 | 13.08 | 9.42 | 1 | 8.42 | 37.4222 | Capped | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
MCRCD2;DC SYS01 [Rect1&2] | NORTH WEST | MANCHESTER | Redstream Optical Network Site | MCRCD2 | Eaton Powerware APR48-ES | 36.6 | 48 | 366 | 19.947 | 2024-05-03 | 75.0007 | 55.0537 | 50.1509 | 30.2039 | 4 | PowerSafe | DDm125-33 | 71.1072 | 51.1602 | 3 | 120 | 90 | 70.053 | 55 |  | 2 | 53.0537 | 28.2039 | 70.7376 | 56.2381 | 49.1602 | 69.1353 | 90 | 40.3845 | 49.6155 | 21.1 | 28.5155 | 31.6839 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
MCRCD2;DC SYS02 [Rect 3&4] | NORTH WEST | MANCHESTER | Redstream Optical Network Site | MCRCD2 | Eaton Powerware APR48-ES | 36.6 | 42 | 375 | 20.4375 | 2024-05-03 | 65.4262 | 44.9887 | 38.1827 | 17.7452 | 4 | PowerSafe | DDm125-33 | 71.1072 | 50.6697 | 3 | 120 | 90 | 69.5625 | 55 |  | 19.1 | 25.8887 | -1.3548 | 39.5693 | -3.5482 | 31.5697 | 44.3973 | [7 empty] | Single | DDm125-33 | 0 | RA | PX | 0 | OPEX | DDm125-33
MCRCD2;DC SYS03 [Rect5] | NORTH WEST | MANCHESTER | Redstream Optical Network Site | MCRCD2 | Eaton Powerware APR48-ES | 36.6 | 27 | 0 | 0 | 0 | 41.4898 | 41.4898 | 42.9242 | 42.9242 | 2 | Chloride | VH34 | 18.4464 | 18.4464 | 3 | 120 | 90 | 90 | 55 |  | 0 | [13 empty] | Single | VH34 | 0 | 0 | 0 | 0 | 0 | VH34
MCRN11;DC SYS01a | NORTH WEST | MANCHESTER | Capped | MCRN11 | Eaton Powerware APR48-ES | 36.6 | 64 | 916 | 49.922 | 2024-05-03 | 100.5329 | 50.6109 | 92.9661 | 43.0441 | 3 | PowerSafe | DDm125-33 | 53.3304 | 3.4084 | 6 | 150 | 112.5 | 62.578 | 39 | Mains Supply; Autonomy; Cooling | 4 | 46.6109 | 39.0441 | 46.3638 | 41.9982 | -0.5916 | -1.1093 | 112.5 | 87.9085 | 24.5915 | 4 | 20.5915 | 18.3036 | Capped | Dual | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
MCRN11;DC SYS01b | NORTH WEST | MANCHESTER | Capped | MCRN11 | Eaton Powerware APR48-ES | 36.6 | 64 | 697 | 37.9865 | 2024-05-03 | 100.5329 | 62.5464 | 92.9661 | 54.9796 | 3 | PowerSafe | DDm125-33 | 53.3304 | 15.3439 | 6 | 150 | 112.5 | 74.5135 | 39 | Mains Supply; Autonomy; Cooling | 0 | 62.5464 | 54.9796 | 62.2148 | 59.1394 | 15.3439 | 28.7714 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
MCRN12;DC SYS01 A | NORTH WEST | MANCHESTER | GIS Migrated - Capped | MCRN12 | Eaton Powerware NPR.48 | 55 | 84 | 1790 | 97.555 | 2024-05-03 | 199.034 | 101.479 | 161.5925 | 64.0375 | 8 | PowerSafe | DDm125-33 | 142.2144 | 44.6594 | 5 | 500 | 375 | 277.445 | 94 | Power | 18.625 | 82.854 | 45.4125 | 41.6281 | 28.1031 | 26.0344 | 18.3064 | 375 | 198.8705 | 176.1295 | 36.85 | 139.2795 | 37.1412 | Capped | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
MCRN12;DC SYS01 B | NORTH WEST | MANCHESTER | GIS Migrated - Capped | MCRN12 | Eaton Powerware NPR.48 | 55 | 84 | 1859 | 101.3155 | 2024-05-03 | 199.034 | 97.7185 | 161.5925 | 60.277 | 8 | PowerSafe | DDm125-33 | 142.2144 | 40.8989 | 5 | 500 | 375 | 273.6845 | 94 | Power | 18.225 | 79.4935 | 42.052 | 39.9397 | 26.0235 | 22.6739 | 15.9435 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
MDBTD1;DC SYS01 | NORTH EAST | MIDDLESBROUGH | Redstream Optical Network Site | MDBTD1 | Power One PMP 25.48 | 45 | 15 | 137 | 7.4665 | 2021-07-14 11:00 | 27.468 | 20.0015 | 27.8495 | 20.383 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 2.6423 | 2 | 30 | 22.5 | 15.0335 | 27 |  | 0 | 20.0015 | 20.383 | 72.8175 | 73.1898 | 2.6423 | 26.1386 | 22.5 | 7.4665 | 15.0335 | 0 | 15.0335 | 66.8156 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
MDE;DC SYS01 | SOUTH EAST | MAIDSTONE | Redstream Optical Network Site | MDE | Eaton Powerware APR48-ES | 36.6 | 23 | 221 | 12.0445 | 2022-04-12 | 35.1067 | 23.0622 | 22.0834 | 10.0389 | 2 | PowerSafe | DDm125-33 | 35.5536 | 23.5091 | 4 | 45 | 33.75 | 21.7055 | 17 |  | 0.3 | 22.7622 | 9.7389 | 64.8372 | 44.1005 | 23.2091 | 65.2792 | 33.75 | 12.0445 | 21.7055 | 0.3 | 21.4055 | 63.4237 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
MDFTB1;DC SYS01 | SCOTLAND | MACDUFF | Capped | MDFTB1 | Eltek FLATPACK2-1800 | 37.5 | 4 | 35 | 1.9075 | 2022-01-03 11:40 | 4.905 | 2.9975 | 5.9132 | 4.0057 | 4 | Enersys | SBS C11F | 3.456 | 1.5485 | 1 | 8 | 6 | 4.0925 | 2 | Space | 4 | -1.0025 | 0.00575 | -20.4383 | 0.097239 | -2.4515 | -70.9346 | 6 | 1.9075 | 4.0925 | 4 | 0.0925 | 1.5417 | Capped | Single | SBS C11F | 0 | 0 | 0 | 0 | 0 | SBS C11F
MKSTN1;DC SYS01 | NORTHERN HOME COUNTIES | MILTON KEYNES | Redstream Optical Network Site | MKSTN1 | Eaton Powerware APR48-ES | 36.6 | 29 | 462 | 25.179 | 2021-12-23 10:00 | 44.6813 | 19.5023 | 34.0516 | 8.8726 | 2 | PowerSafe | DDm125-33 | 35.5536 | 10.3746 | 7 | 72 | 54 | 28.821 | 24 |  | 1 | 18.5023 | 7.8726 | 41.4095 | 23.1196 | 9.3746 | 26.3675 | 54 | 25.179 | 28.821 | 1 | 27.821 | 51.5204 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
NBYCD1;DC SYS01 | THAMES VALLEY | NEWBURY | Capped | NBYCD1 | Eaton Powerware NPR.48 | 55 | 13 | 281 | 15.3145 | 2023-06-21 | 28.776 | 13.4615 | 19.4565 | 4.142 | 3 | PowerSafe | 2CP1000 | 27.0864 | 11.7719 | 3 | 44 | 33 | 17.6855 | 0 | Space | 0.5 | 12.9615 | 3.642 | 45.0427 | 18.7187 | 11.2719 | 41.6146 | 33 | 15.3145 | 17.6855 | 0.5 | 17.1855 | 52.0773 | Capped | Single | 2CP1000 | 0 | 0 | 0 | 0 | 0 | 2CP1000
NECCD1;DC SYS01 | MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | NECCD1 | Eaton Powerware APR48-ES | 36.6 | 8 | 53 | 2.8885 | 2022-03-04 09:00 | 11.1703 | 8.2818 | 10.1697 | 7.2812 | 8 | Enersys | 12V105F | 7.1712 | 4.2827 | 2 | 15 | 11.25 | 8.3615 | 0 |  | 0 | 8.2818 | 7.2812 | 74.1413 | 71.597 | 4.2827 | 59.7208 | 11.25 | 2.8885 | 8.3615 | 0 | 8.3615 | 74.3244 |  | Single | 12V105F | 0 | 0 | 0 | 0 | 0 | 12V105F
NGM;DC SYS03 | MIDLANDS | NOTTINGHAM | Redstream Optical Network Site | NGM | Eaton Powerware APR48-ES | 36.6 | 31 | 579 | 31.5555 | 2021-10-29 17:00 | 47.8728 | 16.3173 | 36.7875 | 5.232 | 3 | PowerSafe | 2CP1400 | 37.908 | 6.3525 | 8 | 133 | 99.75 | 68.1945 | 21 |  | 1 | 15.3173 | 4.232 | 31.9958 | 11.5039 | 5.3525 | 14.1197 | 99.75 | 31.5555 | 68.1945 | 1 | 67.1945 | 67.3629 |  | Single | 2CP1400 | 0 | 0 | 0 | 0 | 0 | 2CP1400
NGMTL1;DC SYS01 | MIDLANDS | NOTTINGHAM | Redstream Optical Network Site | NGMTL1 | Power One PMP 25.48 V3.0 | 50 | 11 | 163.1 | 8.8889 | 2022-06-17 15:16 | 21.8 | 12.911 | 17.5218 | 8.6328 | 3 | PowerSafe | 2DDm85-15 | 15.1632 | 6.2742 | 3 | 60 | 45 | 36.111 | 96 |  | 0 | 12.911 | 8.6328 | 59.225 | 49.2691 | 6.2742 | 41.3781 | 45 | 8.8889 | 36.111 | 0 | 36.111 | 80.2468 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
NRWN51;DC SYS01 | ANGLIA | NORWICH | GIS Migrated | NRWN51 | Eaton Powerware APR48-ES | 36.6 | 7 | 99 | 5.3955 | 2024-05-03 | 9.5746 | 4.1791 | 5.4282 | 0.0327 | 12 | PowerSafe | 12V101F (2 Hour rate) | 18.4291 | 13.0336 | 2 | 15 | 11.25 | 5.8545 | 8 |  | 2.4 | 1.7791 | -2.3673 | 18.5811 | -43.6111 | 10.6336 | 57.7001 | 11.25 | 5.3955 | 5.8545 | 2.4 | 3.4545 | 30.7067 |  | Single | 12V101F | 0 | RA | 0 | 0 | 0 | 12V101F
NRWTN1;DC SYS01 | ANGLIA | NORWICH | Redstream Optical Network Site | NRWTN1 | Eaton Powerware APR48-ES | 36.6 | 18 | 226 | 12.317 | 2022-01-04 18:00 | 27.1279 | 14.8109 | 15.8431 | 3.5261 | 3 | PowerSafe | DDm85-27 | 28.188 | 15.871 | 4 | 30 | 22.5 | 10.183 | 9 |  | 1 | 13.8109 | 2.5261 | 50.9104 | 15.9447 | 14.871 | 52.7565 | 22.5 | 12.317 | 10.183 | 1 | 9.183 | 40.8133 |  | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
NULTB1;DC SYS01 | NORTH WEST | NEWCASTLE-UNDER-LYME | GIS Migrated | NULTB1 | Eaton Powerware APR48-ES | 36.6 | 11 | 101 | 5.5045 | 2024-05-03 | 15.9576 | 10.4531 | 11.663 | 6.1585 | 8 | Enersys | 12V190F | 14.9126 | 9.4081 | 3 | 14 | 10.5 | 4.9955 | 6 |  | 1.7 | 8.7531 | 4.4585 | 54.8522 | 38.2277 | 7.7081 | 51.6886 | 10.5 | 5.5045 | 4.9955 | 1.7 | 3.2955 | 31.3857 |  | Single | 12V190F | 0 | RA | 0 | 0 | 0 | 12V190F
NWCN05;DC SYS01a | NORTH EAST | NEWCASTLE | GIS Migrated | NWCN05 | Eaton Powerware APR48-ES | 36.6 | 32 | 376 | 20.492 | 2024-05-03 | 49.4686 | 28.9766 | 35.6757 | 15.1837 | 4 | PowerSafe | DDm100-25 | 42.2496 | 21.7576 | 3 | 60 | 45 | 24.508 | 40 |  | 10.1 | 18.8766 | 5.0837 | 38.1587 | 14.2498 | 11.6576 | 27.5922 | 45 | 35.316 | 9.684 | 21.3 | -11.616 | -25.8133 |  | Single | DDm100-25 | 0 | RA | 0 | 0 | OPEX | DDm100-25
NWCN05;DC SYS01b | NORTH EAST | NEWCASTLE | GIS Migrated | NWCN05 | Eaton Powerware APR48-ES | 36.6 | 24 | 272 | 14.824 | 2024-05-03 | 36.7025 | 21.8785 | 17.5381 | 2.7141 | 4 | PowerSafe | DDm100-27 | 45.7056 | 30.8816 | 3 | 60 | 45 | 30.176 | 40 |  | 11.2 | 10.6785 | -8.4859 | 29.0947 | -48.3855 | 19.6816 | 43.0617 | [7 empty] | Single | DDm100-27 | [5 empty] | DDm100-27
NWCNY1;DC SYS01 | NORTH EAST | NORTH SHIELDS | Redstream Optical Network Site | NWCNY1 | Eaton Powerware R2948 | 60.4 | 8 | 132 | 7.194 | 2022-03-18 12:00 | 18.4341 | 11.2401 | 16.5571 | 9.3631 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 2.9148 | 2 | 30 | 22.5 | 15.306 | 24 |  | 0 | 11.2401 | 9.3631 | 60.9745 | 56.5504 | 2.9148 | 28.8343 | 22.5 | 7.194 | 15.306 | 0 | 15.306 | 68.0267 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
NWPDN1;DC SYS01 | WALES | NEWPORT | Capped | NWPDN1 | Eaton Powerware NPR.48 | 55 | 6 | 154 | 8.393 | 2021-12-02 14:00 | 11.99 | 3.597 | 9.3369 | 0.94394 | 4 | Yuasa | EN320 | 11.664 | 3.271 | 4 | 30 | 22.5 | 14.107 | 3 | Space | 0 | 3.597 | 0.94394 | 30 | 10.1097 | 3.271 | 28.0436 | 22.5 | 8.393 | 14.107 | 0 | 14.107 | 62.6978 | Capped | Single | EN320 | 0 | 0 | 0 | 0 | 0 | EN320
OHB;DC SYS01;PSU1 | WALES | SWANSEA | Redstream Optical Network Site | OHB | Duvine DD686 | 75 | 9 | 175 | 9.5375 | 2021-06-08 10:00 | 26.16 | 16.6225 | 20.6555 | 11.118 | 2 | PowerSafe | DDm85-27 | 18.792 | 9.2545 | 3 | 60 | 45 | 35.4625 | 31 |  | 2 | 14.6225 | 9.118 | 55.8964 | 44.1432 | 7.2545 | 38.6042 | 45 | 19.3475 | 25.6525 | 2 | 23.6525 | 52.5611 |  | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
OHB;DC SYS02;PSU2 | WALES | SWANSEA | Redstream Optical Network Site | OHB | Duvine DD686 | 75 | 7 | 180 | 9.81 | 2021-06-08 12:00 | 19.62 | 9.81 | 12.4805 | 2.6705 | 2 | PowerSafe | DDm85-27 | 18.792 | 8.982 | 3 | 60 | 45 | 35.19 | 31 |  | 0 | 9.81 | 2.6705 | 50 | 21.3974 | 8.982 | 47.7969 | [7 empty] | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
OKNN01-DCSYS01a | SOUTH WEST | OKEHAMPTON | GIS Migrated | OKNN01 | Eaton Powerware APR48-ES | 36.6 | 22 | 90 | 4.905 | 2024-05-03 | 33.511 | 28.606 | 27.0647 | 22.1597 | 2 | PowerSafe | DDm85-33 | 22.9824 | 18.0774 | 3 | 52 | 39 | 34.095 | 7 |  | 7 | 21.606 | 15.1597 | 64.4743 | 56.0128 | 11.0774 | 48.1995 | 39 | 6.54 | 32.46 | 14.4 | 18.06 | 46.3077 |  | Dual | DDm85-33 | 0 | RA | 0 | AM | 0 | DDm85-33
OKNN01-DCSYS01b | SOUTH WEST | OKEHAMPTON | GIS Migrated | OKNN01 | Eaton Powerware APR48-ES | 36.6 | 22 | 30 | 1.635 | 2024-05-03 | 33.511 | 31.876 | 27.0647 | 25.4297 | 2 | PowerSafe | DDm85-33 | 22.9824 | 21.3474 | 3 | 52 | 39 | 37.365 | 7 |  | 7.4 | 24.476 | 18.0297 | 73.0387 | 66.617 | 13.9474 | 60.6873 | [7 empty] | Dual | DDm85-33 | 0 | 0 | 0 | 0 | 0 | DDm85-33
PCOTN1;DC SYS A;FLAG | SOUTH WEST | PENZANCE | Redstream Optical Network Site | PCOTN1 | Duvine DD686 | 75 | 8 | 150 | 8.175 | 2020-01-10 | 22.89 | 14.715 | 11.1725 | 2.9975 | 2 | PowerSafe | DDm100-33 | 28.1232 | 19.9482 | 11 | 150 | 116.25 | 108.075 | 66 |  | 2 | 12.715 | 0.9975 | 55.5483 | 8.9282 | 17.9482 | 63.8199 | 116.25 | 28.34 | 87.91 | 4 | 83.91 | 72.1806 |  | Dual | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
PCOTN1;DC SYS A;GEMINI | SOUTH WEST | PENZANCE | Redstream Optical Network Site | PCOTN1 | Duvine DD686 | 75 | 11 | 20 | 1.09 | 2021-09-22 15:00 | 32.7 | 31.61 | 19.075 | 17.985 | 2 | PowerSafe | DDm125-33 | 35.5536 | 34.4636 | 11 | 150 | 116.25 | 115.16 | 66 |  | 2 | 29.61 | 15.985 | 90.5505 | 83.8008 | 32.4636 | 91.3089 | [7 empty] | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
PCOTN1;DC SYS B;FLAG | SOUTH WEST | PENZANCE | Redstream Optical Network Site | PCOTN1 | Duvine DD686 | 75 | 8 | 150 | 8.175 | 2020-01-10 | 22.89 | 14.715 | 11.1725 | 2.9975 | 2 | PowerSafe | DDm100-33 | 28.1232 | 19.9482 | 11 | 150 | 116.25 | 108.075 | 66 |  | 0 | 14.715 | 2.9975 | 64.2857 | 26.8293 | 19.9482 | 70.9315 | [7 empty] | Dual | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
PCOTN1;DC SYS B;GEMINI | SOUTH WEST | PENZANCE | Redstream Optical Network Site | PCOTN1 | Duvine DD686 | 75 | 10 | 200 | 10.9 | 2021-09-22 16:00 | 29.43 | 18.53 | 14.9875 | 4.0875 | 2 | PowerSafe | DDm125-33 | 35.5536 | 24.6536 | 11 | 150 | 116.25 | 105.35 | 66 |  | 0 | 18.53 | 4.0875 | 62.963 | 27.2727 | 24.6536 | 69.3421 | [7 empty] | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
PLY-DCSYS01a | SOUTH WEST | PLYMOUTH | GIS Migrated | PLY | Eaton Powerware APR48-ES | 36.6 | 30 | 69 | 3.7605 | 2024-05-03 | 46.277 | 42.5165 | 41.4963 | 37.7358 | 2 | PowerSafe | DDm125-25 | 26.6544 | 22.8939 | 7 | 133.1 | 99.825 | 96.0645 | 49 |  | 11.8 | 30.7165 | 25.9358 | 66.3753 | 62.5015 | 11.0939 | 41.6213 | 99.825 | 3.7605 | 96.0645 | 11.8 | 84.2645 | 84.4122 |  | Dual | DDm125-25 | 0 | RA | 0 | AM | 0 | DDm125-25
PLY-DCSYS01b | SOUTH WEST | PLYMOUTH | GIS Migrated | PLY | Eaton Powerware APR48-ES | 36.6 | 30 | 180 | 9.81 | 2024-05-03 | 46.277 | 36.467 | 41.4963 | 31.6863 | 2 | PowerSafe | DDm125-25 | 26.6544 | 16.8444 | 7 | 133.1 | 99.825 | 90.015 | 49 |  | 12.5 | 23.967 | 19.1863 | 51.7903 | 46.2362 | 4.3444 | 16.299 | 99.825 | 9.81 | 90.015 | 12.5 | 77.515 | 77.6509 |  | Dual | DDm125-25 | 0 | 0 | 0 | 0 | 0 | DDm125-25
PNRTN1;DC SYS01 | NORTH WEST | PENRITH | GIS MIGRATING - CAPPED | PNRTN1 | Harmer & Simmons SC3A/50/100 | 100 | 2 | 6.4 | 0.3488 | 2022-02-24 14:00 | 4.36 | 4.0112 | 0.4142 | 0.0654 | 2 | PowerSafe | 2V460 | 7.992 | 7.6432 | 2 | 12 | 9 | 8.6512 | 8 | Space; Power; Air Con | 0 | 4.0112 | 0.0654 | 92 | 15.7895 | 7.6432 | 95.6356 | 9 | 0.3488 | 8.6512 | 0 | 8.6512 | 96.1244 | Capped | Single | 2V460 | 0 | 0 | 0 | 0 | 0 | 2V460
POLN02-DCSYS01a | SOUTH WEST | POOLE | Capped | POLN02 | Eaton Powerware APR48-ES | 36.6 | 32 | 273 | 14.8785 | 2024-05-03 | 49.4686 | 34.5901 | 40.0357 | 25.1572 | 2 | PowerSafe | DDm125-33 | 35.5536 | 20.6751 | 4 | 90 | 67.5 | 52.6215 | 25 | Autonomy | 10.15 | 24.4401 | 15.0072 | 49.4052 | 37.4845 | 10.5251 | 29.6035 | 67.5 | 17.113 | 50.387 | 20.6 | 29.787 | 44.1289 | Capped | Dual | DDm125-33 | 0 | RA | 0 | AM | 0 | DDm125-33
POLN02-DCSYS01b | SOUTH WEST | POOLE | Capped | POLN02 | Eaton Powerware APR48-ES | 36.6 | 32 | 41 | 2.2345 | 2024-05-03 | 49.4686 | 47.2341 | 40.0357 | 37.8012 | 2 | PowerSafe | DDm125-33 | 35.5536 | 33.3191 | 4 | 90 | 67.5 | 65.2655 | 25 | Autonomy | 10.45 | 36.7841 | 27.3512 | 74.3585 | 68.317 | 22.8691 | 64.3229 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
PRDTB1;DC SYS01 | SCOTLAND | PETERHEAD | Redstream Optical Network Site | PRDTB1 | Eltek FLATPACK2-1800 | 37.5 | 4 | 23 | 1.2535 | 2022-01-03 14:20 | 4.905 | 3.6515 | 3.1229 | 1.8694 | 6 | Enersys | 12V92F | 5.1062 | 3.8527 | 2 | 6.7 | 5.025 | 3.7715 | 7 |  | 1 | 2.6515 | 0.86935 | 54.0571 | 27.8384 | 2.8527 | 55.8677 | 5.025 | 1.2535 | 3.7715 | 1 | 2.7715 | 55.1542 |  | Single | 12V92F | 0 | 0 | 0 | 0 | 0 | 12V92F
PRLN02;DC SYS01 | LONDON | LONDON | Redstream Optical Network Site | PRLN02 | Eaton Powerware APR48-ES | 36.6 | 15 | 257 | 14.0065 | 2021-12-01 | 22.3406 | 8.3341 | 18.9333 | 4.9268 | 11 | PowerSafe | SBS XL 150F-FT | 42.863 | 28.8565 | 2 | 50 | 37.5 | 23.4935 | 5 |  | 5.4 | 2.9341 | -0.4732 | 13.1336 | -2.4993 | 23.4565 | 54.7244 | 37.5 | 14.0065 | 23.4935 | 5.4 | 18.0935 | 48.2493 |  | Single | SBS XL 150F-FT | 0 | 0 | 0 | 0 | 0 | SBS XL 150F-FT
PTBTN1;DC SYS01 | ANGLIA | PETERBOROUGH | Capped | PTBTN1 | Eaton Powerware APR48-ES | 36.6 | 26 | 379 | 20.6555 | 2022-08-09 | 39.894 | 19.2385 | 33.1905 | 12.535 | 3 | PowerSafe | DDm85-25 | 26.1144 | 5.4589 | 3 | 81 | 60.75 | 40.0945 | 9 | Space; Autonomy | 3 | 16.2385 | 9.535 | 40.7041 | 28.7281 | 2.4589 | 9.4159 | 60.75 | 20.6555 | 40.0945 | 3 | 37.0945 | 61.0609 | Capped | Single | DDm85-25 | 0 | 0 | 0 | 0 | 0 | DDm85-25
PTHTL1;DC SYS01 | SCOTLAND | PERTH | Redstream Optical Network Site | PTHTL1 | Eaton Powerware APR48 | 31 | 11 | 77 | 4.1965 | 2024-05-03 | 13.516 | 9.3195 | 10.355 | 6.1585 | 12 | PowerSafe | 12V101F (4 hour Rate) | 10.7568 | 6.5603 | 2 | 15 | 11.25 | 7.0535 | 3 |  | 4 | 5.3195 | 2.1585 | 39.3571 | 20.845 | 2.5603 | 23.8017 | 11.25 | 4.1965 | 7.0535 | 4 | 3.0535 | 27.1422 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
PTMDN1;DC SYS01 | SOUTH | PORTSMOUTH | Redstream Optical Network Site | PTMDN1 | Eaton Powerware APR48-ES | 36.6 | 12 | 124 | 6.758 | 2023-03-07 | 17.5534 | 10.7954 | 11.2815 | 4.5235 | 3 | PowerSafe | 2CP650 | 17.7552 | 10.9972 | 3 | 16 | 12 | 5.242 | 1 |  | 0 | 10.7954 | 4.5235 | 61.5002 | 40.0966 | 10.9972 | 61.9379 | 12 | 6.758 | 5.242 | 0 | 5.242 | 43.6833 |  | Single | 2CP650 | 0 | 0 | 0 | 0 | 0 | 2CP650
PTMN03;DC SYS01 | SOUTH | PORTSMOUTH | GIS Migrated | PTMN03 | Eaton Powerware APR48-ES | 36.6 | 35 | 333 | 18.1485 | 2024-05-03 | 54.2558 | 36.1073 | 35.1198 | 16.9713 | 3 | PowerSafe | DDm125-33 | 53.3304 | 35.1819 | 3 | 60 | 45 | 26.8515 | 278 |  | 2.7 | 33.4073 | 14.2713 | 61.5737 | 40.6361 | 32.4819 | 60.9069 | 45 | 18.1485 | 26.8515 | 2.7 | 24.1515 | 53.67 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
RATE02;DC SYS01 | MIDLANDS | RATCLIFFE ON SOAR | Redstream Optical Network Site | RATE02 | Advance MRF2800 | 50 | 4 | 25 | 1.3625 | 2021-10-21 16:00 | 6.54 | 5.1775 | 5.995 | 4.6325 | 4 | PowerSafe | 12V101F (4 hour Rate) | 3.5856 | 2.2231 | 2 | 10 | 7.5 | 6.1375 | 3 |  | 0 | 5.1775 | 4.6325 | 79.1667 | 77.2727 | 2.2231 | 62.0008 | 7.5 | 3.488 | 4.012 | 0 | 4.012 | 53.4933 |  | Dual | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
RATE02;DC SYS02 | MIDLANDS | RATCLIFFE ON SOAR | Redstream Optical Network Site | RATE02 | Advance MRF2800 | 50 | 4 | 39 | 2.1255 | 2021-10-21 17:00 | 6.54 | 4.4145 | 6.431 | 4.3055 | 4 | Enersys | 12V100F | 3.9053 | 1.7798 | 2 | 10 | 7.5 | 5.3745 | 3 |  | 0 | 4.4145 | 4.3055 | 67.5 | 66.9492 | 1.7798 | 45.5737 | [7 empty] | Dual | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
RCR;DC SYS01 | SOUTH EAST | ROCHESTER | GIS Migrated | RCR | Eaton Powerware APR48-ES | 36.6 | 23 | 233 | 12.6985 | 2022-11-30 | 35.1067 | 22.4082 | 22.0834 | 9.3849 | 2 | PowerSafe | DDm125-33 | 35.5536 | 22.8551 | 7 | 45 | 33.75 | 21.0515 | 17 |  | 2.7 | 19.7082 | 6.6849 | 56.138 | 30.2712 | 20.1551 | 56.6893 | 33.75 | 12.6985 | 21.0515 | 2.7 | 18.3515 | 54.3748 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
RDGCD2;DC SYS01 | THAMES VALLEY | READING | Redstream Optical Network Site | RDGCD2 | Eaton Powerware NPR.48 | 55 | 25 | 424 | 23.108 | 2021-08-20 09:00 | 57.552 | 34.444 | 39.24 | 16.132 | 3 | PowerSafe | DDm125-33 | 53.3304 | 30.2224 | 3 | 42 | 31.5 | 8.392 | 34 |  | 12 | 22.444 | 4.132 | 38.9978 | 10.5301 | 18.2224 | 34.1689 | 31.5 | 23.108 | 8.392 | 12 | -3.608 | -11.454 |  | Single | DDm125-33 | 0 | 0 | 0 | AM | 0 | DDm125-33
RDG;DC SYS01 | THAMES VALLEY | READING | Redstream Optical Network Site | RDG | Duvine DD686 | 75 | 12 | 225 | 12.2625 | 2023-03-29 | 35.97 | 23.7075 | 32.918 | 20.6555 | 2 | PowerSafe | DDm85-27 | 18.792 | 6.5295 | 8 | 48 | 36 | 23.7375 | 27 |  | 0 | 23.7075 | 20.6555 | 65.9091 | 62.7483 | 6.5295 | 34.7462 | 36 | 12.2625 | 23.7375 | 0 | 23.7375 | 65.9375 |  | Single | DDm85-27 | 0 | 0 | 0 | 0 | 0 | DDm85-27
RFDN11;DC SYS01 | LONDON | ROMFORD | Redstream Optical Network Site | RFDN11 | Eaton Powerware APR48-ES | 36.6 | 9 | 39 | 2.1255 | 2024-05-03 | 12.7661 | 10.6406 | 9.4721 | 7.3466 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 7.9833 | 2 | 15 | 11.25 | 9.1245 | 35 |  | 0 | 10.6406 | 7.3466 | 83.3504 | 77.5604 | 7.9833 | 78.9738 | 11.25 | 2.1255 | 9.1245 | 0 | 9.1245 | 81.1067 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
SBHN01;DC SYS01 | NORTH EAST | SCARBOROUGH | Redstream Optical Network Site | SBHN01 | Duvine DD686 | 75 | 8 | 150 | 8.175 | 2022-05-17 13:30 | 22.89 | 14.715 | 22.127 | 13.952 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 1.9338 | 4 | 90 | 67.5 | 59.325 | 84 |  | 0 | 14.715 | 13.952 | 64.2857 | 63.0542 | 1.9338 | 19.1299 | 67.5 | 8.175 | 59.325 | 0 | 59.325 | 87.8889 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
SDN;DC SYS01 | SOUTH WEST | SWINDON | Redstream Optical Network Site | SDN | Duvine DD686 | 75 | 15 | 340 | 18.53 | 2023-09-13 | 45.78 | 27.25 | 22.345 | 3.815 | 4 | PowerSafe | DDm100-33 | 56.2464 | 37.7164 | 10 | 83 | 62.25 | 43.72 | 6 |  | 0 | 27.25 | 3.815 | 59.5238 | 17.0732 | 37.7164 | 67.0557 | 62.25 | 18.53 | 43.72 | 0 | 43.72 | 70.2329 |  | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
SDNN06;DC SYS02 | SOUTH WEST | SWINDON | GIS Migrated | SDNN06 | Eaton Powerware APR48-ES | 36.6 | 83 | 1256 | 68.452 | 2022-10-12 | 130.8523 | 62.4003 | 102.5254 | 34.0734 | 7 | PowerSafe | DDm100-33 (2 Hour rate) | 155.5848 | 87.1328 | 11 | 548 | 411 | 342.548 | 61 |  | 36.5 | 25.9003 | -2.4266 | 19.7936 | -2.3668 | 50.6328 | 32.5435 | 411 | 115.4855 | 295.5145 | 47 | 248.5145 | 60.4658 |  | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
SDNN06;DC SYS03 | SOUTH WEST | SWINDON | GIS Migrated | SDNN06 | Eaton Powerware NPR.48 | 55 | 42 | 863 | 47.0335 | 2022-10-12 | 98.318 | 51.2845 | 90.1975 | 43.164 | 3 | PowerSafe | DDm125-33 (2hr rate) | 85.212 | 38.1785 | 11 | 548 | 411 | 363.9665 | 61 |  | 10.5 | 40.7845 | 32.664 | 41.4822 | 36.2139 | 27.6785 | 32.4819 | [7 empty] | Single | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
SDNN11;DC SYS01 | SOUTH WEST | SWINDON | GIS Migrated | SDNN06 | Eaton Powerware APR48 | 31 | 5 | 83 | 4.5235 | 2022-06-07 13:30 | 5.4064 | 0.8829 | 4.578 | 0.0545 | 4 | PowerSafe | 12V101F (2 Hour rate) | 6.143 | 1.6195 | 11 | 548 | 411 | 406.4765 | 61 |  | 0 | 0.8829 | 0.0545 | 16.3306 | 1.1905 | 1.6195 | 26.3638 | 411 | 4.5235 | 406.4765 | 0 | 406.4765 | 98.8994 |  | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
SDNN13;DC SYS01 | SOUTH WEST | SWINDON | GIS Migrated | SDNN13 | Eaton Powerware APR48-ES | 36.6 | 18 | 148 | 8.066 | 2023-08-23 | 27.1279 | 19.0619 | 24.6449 | 16.5789 | 2 | PowerSafe | DDm85-21(2 Hour Rate) | 23.0256 | 14.9596 | 2 | 50 | 37.5 | 29.434 | 4 |  | 10.2 | 8.8619 | 6.3789 | 32.6672 | 25.8832 | 4.7596 | 20.6709 | 37.5 | 8.066 | 29.434 | 10.2 | 19.234 | 51.2907 |  | Single | DDm85-21 | 0 | 0 | 0 | 0 | 0 | DDm85-21
SHD;DC SYS01 | NORTH EAST | SHEFFIELD | Redstream Optical Network Site | SHD | Eaton Powerware APR48-ES | 36.6 | 30 | 365 | 19.8925 | 2024-05-03 | 46.277 | 26.3845 | 36.0463 | 16.1538 | 2 | PowerSafe | DDm125-33 | 35.5536 | 15.6611 | 8 | 84 | 63 | 43.1075 | 6 |  | 0.25 | 26.1345 | 15.9038 | 56.4741 | 44.1205 | 15.4111 | 43.3461 | 63 | 19.8925 | 43.1075 | 0.25 | 42.8575 | 68.0278 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
SHDTR1;DC SYS01 | NORTH EAST | SHEFFIELD | Redstream Optical Network Site | SHDTR1 | Eaton Powerware APR48-ES | 36.6 | 26 | 262 | 14.279 | 2024-05-03 | 39.894 | 25.615 | 28.0675 | 13.7885 | 2 | PowerSafe | DDm125-33 | 35.5536 | 21.2746 | 6 | 150 | 112.5 | 98.221 | 21 |  | 7.2 | 18.415 | 6.5885 | 46.1598 | 23.4738 | 14.0746 | 39.587 | 112.5 | 14.279 | 98.221 | 7.2 | 91.021 | 80.9076 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
SHTN03;DC SYS02 | SOUTH | SOUTHAMPTON | GIS Migrated | SHTN03 | Eaton Powerware APR48-ES | 36.6 | 37 | 466 | 25.397 | 2024-05-03 | 57.4474 | 32.0504 | 39.1092 | 13.7122 | 3 | PowerSafe | DDm125-33 | 53.3304 | 27.9334 | 12 | 112.5 | 84.375 | 58.978 | 69 |  | 3.7 | 28.3504 | 10.0122 | 49.3502 | 25.6006 | 24.2334 | 45.4401 | 84.375 | 25.397 | 58.978 | 3.7 | 55.278 | 65.5147 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
SLO;DC SYS01 | THAMES VALLEY | SLOUGH | Capped | SLO | Eaton Powerware APR48-ES | 36.6 | 35 | 518 | 28.231 | 2024-05-03 | 54.2558 | 26.0248 | 35.1198 | 6.8888 | 3 | PowerSafe | DDm125-33 | 53.3304 | 25.0994 | 8 | 84 | 63 | 34.769 | 13 | DC Power | 3.5 | 22.5248 | 3.3888 | 41.516 | 9.6493 | 21.5994 | 40.5011 | 63 | 28.231 | 34.769 | 3.5 | 31.269 | 49.6333 | Capped | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
SMHN02;DC SYS01 | LONDON | LONDON | Capped | SMHN02 | Duvine DD686 | 75 | 18 | 570 | 31.065 | 2022-03-23 08:30 | 55.59 | 24.525 | 48.2325 | 17.1675 | 3 | PowerSafe | DDm100-27 | 34.2792 | 3.2142 | 3 | 140 | 105 | 73.935 | 3 | Space | 0 | 24.525 | 17.1675 | 44.1176 | 35.5932 | 3.2142 | 9.3765 | 105 | 31.065 | 73.935 | 0 | 73.935 | 70.4143 | Capped | Single | DDm100-27 | 0 | 0 | 0 | 0 | 0 | DDm100-27
SNDTM1;DC SYS01 | NORTH EAST | SUNDERLAND | Redstream Optical Network Site | SNDTM1 | Eaton Powerware R2948 | 60.4 | 6 | 92 | 5.014 | 2024-03-05 | 13.1672 | 8.1532 | 13.189 | 8.175 | 2 | PowerSafe | 2DDm50-13 | 5.2272 | 0.2132 | 3 | 60 | 45 | 39.986 | 9 |  | 0 | 8.1532 | 8.175 | 61.9205 | 61.9835 | 0.2132 | 4.0787 | 45 | 5.014 | 39.986 | 0 | 39.986 | 88.8578 |  | Single | 2DDm50-13 | 0 | 0 | 0 | 0 | 0 | 2DDm50-13
SOL;DC SYS01 | MIDLANDS | SOLIHULL | Redstream Optical Network Site | SOLN02 | Eaton Powerware HDR48-ES | 55 | 15 | 240 | 13.08 | 2024-05-03 | 33.572 | 20.492 | 20.165 | 7.085 | 2 | PowerSafe | DDm125-33 | 35.5536 | 22.4736 | 3 | 60 | 45 | 31.92 | 38 |  | 2 | 18.492 | 5.085 | 55.0816 | 25.217 | 20.4736 | 57.5852 | 45 | 13.08 | 31.92 | 2 | 29.92 | 66.4889 |  | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
SOSTN1;DC SYS01 | ANGLIA | SOUTHEND | Redstream Optical Network Site | SOSTN1 | Eaton Powerware APR48-ES | 36.6 | 10 | 130 | 7.085 | 2021-02-04 | 14.3618 | 7.2768 | 8.6873 | 1.6023 | 2 | PowerSafe | DDm85-21 | 14.4288 | 7.3438 | 3 | 26 | 19.5 | 12.415 | 30 |  | 2 | 5.2768 | -0.3977 | 36.7421 | -4.5779 | 5.3438 | 37.0357 | 19.5 | 7.085 | 12.415 | 2 | 10.415 | 53.4103 |  | Single | DDm85-21 | 0 | 0 | 0 | 0 | 0 | DDm85-21
SOT;DC SYS01 | MIDLANDS | STOKE | Redstream Optical Network Site | SOT | Eaton Powerware APR48-ES | 36.6 | 12 | 215 | 11.7175 | 2024-05-03 | 17.5534 | 5.8359 | 8.8617 | -2.8558 | 2 | PowerSafe | DDm100-25 | 21.1248 | 9.4073 | 5 | 24 | 18 | 6.2825 | 22 |  | 1 | 4.8359 | -3.8558 | 27.5495 | -43.5108 | 8.4073 | 39.7982 | 18 | 11.7175 | 6.2825 | 1 | 5.2825 | 29.3472 |  | Single | DDm100-25 | 0 | 0 | 0 | 0 | 0 | DDm100-25
SQYN01;DC SYS01 | LONDON | LONDON | GIS Migrated | SQYN01 | Eaton Powerware APR48-ES | 36.6 | 29 | 225 | 12.2625 | 2024-05-03 | 44.6813 | 32.4188 | 31.3266 | 19.0641 | 3 | PowerSafe | DDm125-25 | 39.9816 | 27.7191 | 6 | 250 | 187.5 | 175.2375 | 104 |  | 4 | 28.4188 | 15.0641 | 63.6033 | 48.0872 | 23.7191 | 59.325 | 187.5 | 98.2635 | 89.2365 | 4 | 85.2365 | 45.4595 |  | Single | DDm125-25 | 0 | 0 | 0 | 0 | 0 | DDm125-25
SQYN01;DC SYS02 | LONDON | LONDON | GIS Migrated | SQYN01 | Eaton Powerware APR48-ES | 36.6 | 45 | 798 | 43.491 | 2024-05-03 | 70.2134 | 26.7224 | 52.8868 | 9.3958 | 4 | PowerSafe | DDm100-33 | 56.2464 | 12.7554 | 6 | 250 | 187.5 | 144.009 | 104 |  | 0 | 26.7224 | 9.3958 | 38.0589 | 17.7659 | 12.7554 | 22.6777 | [7 empty] | Single | DDm100-33 | 0 | 0 | 0 | 0 | 0 | DDm100-33
SQYN01;DC SYS03 | LONDON | LONDON | GIS Migrated | SQYN01 | Eaton Powerware APR48-ES | 36.6 | 63 | 780 | 42.51 | 2024-05-03 | 98.9371 | 56.4271 | 90.9714 | 48.4614 | 3 | PowerSafe | DDm125-33 | 53.3304 | 10.8204 | 6 | 250 | 187.5 | 144.99 | 104 |  | 0 | 56.4271 | 48.4614 | 57.0333 | 53.271 | 10.8204 | 20.2894 | [7 empty] | Single | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
SQYN02;DC SYS08a | LONDON | LONDON | GIS Migrated | SQYN02 | Eaton Powerware APR48-ES | 36.6 | 63 | 821 | 44.7445 | 2024-05-03 | 98.9371 | 54.1926 | 79.3902 | 34.6457 | 5 | PowerSafe | DDm125-27 | 72.144 | 27.3995 | 7 | 498 | 373.5 | 328.7555 | 94 |  | 17.05 | 37.1426 | 17.5957 | 37.5416 | 22.1635 | 10.3495 | 14.3456 | 373.5 | 187.48 | 186.02 | 45.1 | 140.92 | 37.7296 |  | Dual | DDm125-27 | P-Core | 0 | 0 | 0 | 0 | DDm125-27
SQYN02;DC SYS08b | LONDON | LONDON | GIS Migrated | SQYN02 | Eaton Powerware APR48-ES | 36.6 | 64 | 809 | 44.0905 | 2024-05-03 | 100.5329 | 56.4424 | 71.1661 | 27.0756 | 5 | PowerSafe | DDm125-33 | 88.884 | 44.7935 | 7 | 498 | 373.5 | 329.4095 | 94 |  | 16.55 | 39.8924 | 10.5256 | 39.6809 | 14.7902 | 28.2435 | 31.7757 | [7 empty] | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
SQYN02;DC SYS09a | LONDON | LONDON | GIS Migrated | SQYN02 | Eaton Powerware APR48-ES | 36.6 | 72 | 905 | 49.3225 | 2024-05-03 | 113.299 | 63.9765 | 76.2237 | 26.9012 | 6 | PowerSafe | DDm125-33 | 106.6608 | 57.3383 | 7 | 498 | 373.5 | 324.1775 | 94 |  | 5.75 | 58.2265 | 21.1512 | 51.3919 | 27.7488 | 51.5883 | 48.3667 | 373.5 | 98.645 | 274.855 | 11.5 | 263.355 | 70.51 |  | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
SQYN02;DC SYS09b | LONDON | LONDON | GIS Migrated | SQYN02 | Eaton Powerware APR48-ES | 36.6 | 72 | 905 | 49.3225 | 2024-05-03 | 113.299 | 63.9765 | 76.2237 | 26.9012 | 6 | PowerSafe | DDm125-33 | 106.6608 | 57.3383 | 7 | 498 | 373.5 | 324.1775 | 94 |  | 5.75 | 58.2265 | 21.1512 | 51.3919 | 27.7488 | 51.5883 | 48.3667 | [7 empty] | Single | DDm125-33 | P-Core | 0 | 0 | 0 | 0 | DDm125-33
STEDN1;DC SYS01 | NORTHERN HOME COUNTIES | STEVENAGE | Capped | STEDN1 | Eaton Powerware APR48-ES | 36.6 | 12 | 109 | 5.9405 | 2024-05-03 | 17.5534 | 11.6129 | 21.1569 | 15.2164 | 3 | Enersys | SBS480 EON | 12.9276 | 6.9871 | 2 | 15 | 11.25 | 5.3095 | 1 | Space | 0 | 11.6129 | 15.2164 | 66.1575 | 71.9217 | 6.9871 | 54.0479 | 11.25 | 5.9405 | 5.3095 | 0 | 5.3095 | 47.1956 | Capped | Single | SBS480 EON | 0 | 0 | 0 | 0 | 0 | SBS480 EON
STGCD1;DC SYS01 | SCOTLAND | STIRLING | Redstream Optical Network Site | STGCD1 | Duvine DD686 | 75 | 6 | 125 | 6.8125 | 2022-11-08 | 16.35 | 9.5375 | 13.952 | 7.1395 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 3.2963 | 2 | 20 | 15 | 8.1875 | 13 |  | 3 | 6.5375 | 4.1395 | 39.9847 | 29.6696 | 0.2963 | 2.9311 | 15 | 6.8125 | 8.1875 | 3 | 5.1875 | 34.5833 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
SWNN03;DC SYS01 | WALES | SWANSEA | GIS Migrated | SWNN03 | Eaton Powerware APR48-ES | 36.6 | 10 | 182 | 9.919 | 2024-05-03 | 14.3618 | 4.4428 | 6.8343 | -3.0847 | 2 | PowerSafe | DDm85-25 | 17.4096 | 7.4906 | 2 | 40 | 30 | 20.081 | 5 |  | 3.4 | 1.0428 | -6.4847 | 7.2612 | -94.8846 | 4.0906 | 23.4962 | 30 | 9.919 | 20.081 | 3.4 | 16.681 | 55.6033 |  | Single | DDm85-25 | 0 | RA | 0 | 0 | 0 | DDm85-25
SWY;DC SYS01 | MIDLANDS | SHREWSBURY | Redstream Optical Network Site | SWY | Eaton Powerware APR48-ES | 36.6 | 26 | 341 | 18.5845 | 2021-11-02 10:00 | 39.894 | 21.3095 | 33.6483 | 15.0638 | 2 | FIAMM | 2SLA2000 | 33.3936 | 14.8091 | 2 | 40.5 | 45.5625 | 26.978 | 13 |  | 3 | 18.3095 | 12.0638 | 45.8954 | 35.8526 | 11.8091 | 35.3634 | 45.5625 | 18.5845 | 26.978 | 3 | 23.978 | 52.6266 |  | Single | 2SLA2000 | 0 | 0 | 0 | 0 | 0 | 2SLA2000
TELHS1;DC SYS A;EXT ROOM | LONDON | LONDON | Redstream Optical Network Site | TELHS1 | Benning Tebechop 2700 | 50 | 6 | 159 | 8.6655 | 2022-01-26 10:40 | 10.9 | 2.2345 | 6.5945 | -2.071 | 10 | Enersys | 12V155F | 14.04 | 5.3745 | 4 | 34 | 25.5 | 16.8345 | 2 |  | 1.1 | 1.1345 | -3.171 | 10.4083 | -48.0855 | 4.2745 | 30.4452 | 25.5 | 19.9198 | 5.5802 | 1.1 | 4.4802 | 17.5696 |  | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
TELHS1;DC SYS B;EXT ROOM | LONDON | LONDON | Redstream Optical Network Site | TELHS1 | Benning Tebechop 2700 | 50 | 6 | 131.5 | 7.1668 | 2021-11-04 13:00 | 10.9 | 3.7332 | 6.5945 | -0.57225 | 10 | Enersys | 12V155F | 14.04 | 6.8733 | 4 | 34 | 25.5 | 18.3332 | 2 |  | 0 | 3.7332 | -0.57225 | 34.25 | -8.6777 | 6.8733 | 48.9548 | [7 empty] | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
TELHS1;SYS;A;DC PER02;9D | LONDON | LONDON | Redstream Optical Network Site | TELHS1 | Advance MRF2800 | 50 | 6 | 53 | 2.8885 | 2023-05-12 | 10.9 | 8.0115 | 5.1884 | 2.2999 | 12 | Enersys | 12V155F | 16.848 | 13.9595 | 4 | 34 | 25.5 | 22.6115 | 2 |  | 0 | 8.0115 | 2.2999 | 73.5 | 44.3277 | 13.9595 | 82.8555 | [7 empty] | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
TELHS1;SYS;B;DC PER03;1L | LONDON | LONDON | Redstream Optical Network Site | TELHS1 | Advance MRF2800 | 50 | 4 | 22 | 1.199 | 2023-05-12 | 6.54 | 5.341 | 2.5506 | 1.3516 | 8 | Enersys | 12V155F | 11.232 | 10.033 | 4 | 34 | 25.5 | 24.301 | 2 |  | 0 | 5.341 | 1.3516 | 81.6667 | 52.9914 | 10.033 | 89.3251 | [7 empty] | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
TELHS2;DC SYS01 | LONDON | LONDON | Capped | TELHS2 | Eaton Powerware APR48-3G | 37.5 | 10 | 18 | 0.981 | 2022-02-10 17:00 | 14.715 | 13.734 | 11.4177 | 10.4367 | 8 | FIAMM | 12UMTB160 | 9.4867 | 8.5057 | 2 | 18 | 13.5 | 12.519 | 0 | Space | 0 | 13.734 | 10.4367 | 93.3333 | 91.4081 | 8.5057 | 89.6592 | 13.5 | 0.981 | 12.519 | 0 | 12.519 | 92.7333 | Capped | Single | 12UMTB160 | 0 | 0 | 0 | 0 | 0 | 12UMTB160
TGY;DC SYSA | NORTH EAST | LEEDS | Capped | TGYN04 | Eaton Powerware APR48-ES | 36.6 | 51 | 534 | 29.103 | 2024-05-03 | 79.788 | 50.685 | 67.035 | 37.932 | 3 | PowerSafe | DDm125-33 | 53.3304 | 24.2274 | 4 | 22.2 | 16.65 | -12.453 | 6 | P Core use only, Power | 8.205 | 42.48 | 29.727 | 53.2411 | 44.3455 | 16.0224 | 30.0437 | 91.35 | 63.983 | 27.367 | 16.41 | 10.957 | 11.9945 | Capped | Dual | DDm125-33 | P-Core | 0 | PX | 0 | OPEX | DDm125-33
TGY;DC SYSB **DO NOT CONNECT LOADS** | NORTH EAST | LEEDS | Capped | TGYN04 | Eaton Powerware APR48-ES | 36.6 | 51 | 640 | 34.88 | 2024-05-03 | 79.788 | 44.908 | 67.035 | 32.155 | 3 | PowerSafe | DDm125-33 | 53.3304 | 18.4504 | 4 | 22.2 | 16.65 | -18.23 | 6 | P Core use only, Power | 8.205 | 36.703 | 23.95 | 46.0007 | 35.7276 | 10.2454 | 19.2112 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
THOTC1;DC SYS01 | SCOTTISH HIGHLANDS & ISLANDS | THURSO | GIS MIGRATING | THOTC1 | Eltek FLATPACK2-1800 | 37.5 | 3 | 8 | 0.436 | 2021-10-12 16:50 | 3.27 | 2.834 | 2.7795 | 2.3435 | 3 | Enersys | 12V100F | 2.929 | 2.493 | 2 | 5 | 3.75 | 3.314 | 0 |  | 0 | 2.834 | 2.3435 | 86.6667 | 84.3137 | 2.493 | 85.1142 | 3.75 | 0.436 | 3.314 | 0 | 3.314 | 88.3733 |  | Single | 12V100F | 0 | 0 | 0 | 0 | 0 | 12V100F
TNTTN1-DCSYS01a | SOUTH WEST | TAUNTON | Redstream Optical Network Site | TNTTN1 | Eaton Powerware APR48-ES | 36.6 | 22 | 115 | 6.2675 | 2024-05-03 | 33.511 | 27.2435 | 27.0647 | 20.7972 | 2 | PowerSafe | DDm85-33 | 22.9824 | 16.7149 | 3 | 45 | 33.75 | 27.4825 | 55 |  | 7.4 | 19.8435 | 13.3972 | 59.2148 | 49.5006 | 9.3149 | 40.5306 | 33.75 | 6.2675 | 27.4825 | 7.4 | 20.0825 | 59.5037 |  | Dual | DDm85-33 | 0 | 0 | 0 | 0 | 0 | DDm85-33
TNTTN1-DCSYS01b | SOUTH WEST | TAUNTON | Redstream Optical Network Site | TNTTN1 | Eaton Powerware APR48-ES | 36.6 | 22 | 76 | 4.142 | 2024-05-03 | 33.511 | 29.369 | 27.0647 | 22.9227 | 2 | PowerSafe | DDm85-33 | 22.9824 | 18.8404 | 3 | 45 | 33.75 | 29.608 | 55 |  | 7.7 | 21.669 | 15.2227 | 64.6623 | 56.2456 | 11.1404 | 48.4736 | 33.75 | 4.142 | 29.608 | 7.7 | 21.908 | 64.9126 |  | Dual | DDm85-33 | 0 | 0 | 0 | 0 | 0 | DDm85-33
TRON01;DC SYS01 | SOUTH WEST | TRURO | Redstream Optical Network Site | TRON01 | Eaton Powerware APR48-ES | 36.6 | 6 | 47 | 2.5615 | 2024-05-03 | 7.9788 | 5.4173 | 6.867 | 4.3055 | 3 | Enersys | 12V190F | 5.5922 | 3.0307 | 4 | 24 | 18 | 15.4385 | 65 |  | 0 | 5.4173 | 4.3055 | 67.8962 | 62.6984 | 3.0307 | 54.1955 | 18 | 2.5615 | 15.4385 | 0 | 15.4385 | 85.7694 |  | Single | 12V190F | 0 | 0 | 0 | 0 | 0 | 12V190F
VHXN02;DC SYS01 | LONDON | VAUXHALL | GIS MIGRATING | VHXN02 | Eaton Powerware APR48-ES | 36.6 | 44 | 721 | 39.2945 | 2022-03-07 14:30 | 68.6177 | 29.3232 | 42.1721 | 2.8776 | 4 | PowerSafe | DDm125-33 | 71.1072 | 31.8127 | 4 | 90 | 67.5 | 28.2055 | 1 |  | 7.4 | 21.9232 | -4.5224 | 31.9498 | -10.7237 | 24.4127 | 34.3322 | 67.5 | 39.2945 | 28.2055 | 7.4 | 20.8055 | 30.823 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
WADN01;DC SYS01 | LONDON | CROYDON | Capped | WADN01 | Eaton Powerware APR48-ES | 36.6 | 90 | 78 | 4.251 | 2022-05-11 14:00 | 142.0226 | 137.7716 | 116.4883 | 112.2373 | 4 | PowerSafe | 2CP3000 | 95.6102 | 91.3592 | 4 | 120 | 90 | 85.749 | 8 | Planned Closure | 0 | 137.7716 | 112.2373 | 97.0068 | 96.3507 | 91.3592 | 95.5538 | 90 | 4.251 | 85.749 | 0 | 85.749 | 95.2767 | Capped | Single | 2CP3000 | 0 | 0 | 0 | 0 | 0 | 2CP3000
WAHP; DC SYS A (Feeds WAHP06) | LONDON | WATFORD | GIS Migrated - Capped | WAHP06 | Eaton Powerware APR48-ES | 36.6 | 67 | 1025 | 55.8625 | 2024-05-03 | 105.3202 | 49.4577 | 77.1502 | 21.2877 | 5 | PowerSafe | DDm125-33 | 88.884 | 33.0215 | 4 | 150 | 112.5 | 56.6375 | 9 | Power;Autonomy | 10.025 | 39.4327 | 11.2627 | 37.4408 | 14.5984 | 22.9965 | 25.8725 | 112.5 | 104.5855 | 7.9145 | 21.05 | -13.1355 | -11.676 | Capped | Dual | DDm125-33 | P-Core | RA | PX | 0 | OPEX | DDm125-33
WAHP; DC SYS B (Feeds WAHP06) | LONDON | WATFORD | GIS Migrated - Capped | WAHP06 | Eaton Powerware APR48-ES | 36.6 | 67 | 894 | 48.723 | 2024-05-03 | 105.3202 | 56.5972 | 77.1502 | 28.4272 | 5 | PowerSafe | DDm125-33 | 88.884 | 40.161 | 4 | 150 | 112.5 | 63.777 | 9 | Power;Autonomy | 11.025 | 45.5722 | 17.4022 | 43.2701 | 22.5563 | 29.136 | 32.7798 | [6 empty] | Capped | Dual | DDm125-33 | 0 | 0 | 0 | 0 | 0 | DDm125-33
WAHP;DC SYS A Tx | LONDON | WATFORD | GIS Migrated | WAHP03 | Eaton Powerware APR48-ES | 36.6 | 60 | 355 | 19.3475 | 2024-05-03 | 94.1498 | 74.8023 | 96.4323 | 77.0848 | 3 | PowerSafe | DDm100-27 | 34.2792 | 14.9317 | 5 | 120 | 90 | 70.6525 | 64 |  | 11.83 | 62.9723 | 65.2548 | 66.8852 | 67.669 | 3.1017 | 9.0483 | 90 | 38.477 | 51.523 | 23.66 | 27.863 | 30.9589 |  | Dual | DDm100-27 | 0 | 0 | 0 | 0 | 0 | DDm100-27
WAHP;DC SYS B Tx | LONDON | WATFORD | GIS Migrated | WAHP03 | Eaton Powerware APR48-ES | 36.6 | 60 | 351 | 19.1295 | 2024-05-03 | 94.1498 | 75.0203 | 96.4323 | 77.3028 | 3 | PowerSafe | DDm100-27 | 34.2792 | 15.1497 | 5 | 120 | 90 | 70.8705 | 64 |  | 11.83 | 63.1903 | 65.4728 | 67.1168 | 67.8951 | 3.3197 | 9.6843 | [7 empty] | Dual | DDm100-27 | 0 | 0 | 0 | 0 | 0 | DDm100-27
WAIP;DC SYS01;GND | LONDON | WATFORD | Redstream Optical Network Site | WAIP06 | Eaton Powerware NPR.48 | 55 | 8 | 61 | 3.3245 | 2022-04-22 14:30 | 16.786 | 13.4615 | 19.8925 | 16.568 | 2 | Enersys | 12V125F | 2.2507 | -1.0738 | 4 | 150 | 112.5 | 109.1755 | 6 |  | 0 | 13.4615 | 16.568 | 80.1948 | 83.2877 | -1.0738 | -47.7083 | 112.5 | 3.3245 | 109.1755 | 0 | 109.1755 | 97.0449 |  | Single | 12V125F | 0 | 0 | 0 | 0 | 0 | 12V125F
WCKTR1;DCSYS01 | SCOTTISH HIGHLANDS & ISLANDS | WICK | Redstream Optical Network Site | WCKTR1 | Eaton Powerware APR48-ES | 36.6 | 4 | 40 | 2.18 | 2024-05-03 | 4.7873 | 2.6073 | 3.8749 | 1.6949 | 3 | Enersys | 12V155F | 4.212 | 2.032 | 2 | 6.7 | 5.025 | 2.845 | 5 |  | 1.5 | 1.1073 | 0.19495 | 23.1296 | 5.031 | 0.532 | 12.6306 | 5.025 | 2.18 | 2.845 | 1.5 | 1.345 | 26.7662 |  | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
WHD;DC SYS01 | NORTHERN IRELAND | WHITEHEAD | GIS MIGRATING - CAPPED | WHD | Duvine Dummy 20A | 20 | 3 | 9 | 0.4905 | 2022-06-08 14:00 | 1.744 | 1.2535 | 0.545 | 0.0545 | 3 | PowerSafe | 12V101F (4 hour Rate) | 2.6892 | 2.1987 | 2 | 8 | 6 | 5.5095 | 1 | Space; Power | 0 | 1.2535 | 0.0545 | 71.875 | 10 | 2.1987 | 81.7604 | 6 | 0.4905 | 5.5095 | 0 | 5.5095 | 91.825 | Capped | Single | 12V101F | 0 | 0 | 0 | 0 | 0 | 12V101F
WHHN03;DC SYS01 | THAMES VALLEY | KIDLINGTON | Redstream Optical Network Site | WHHN03 | Eaton Powerware APR48 | 31 | 24 | 438 | 23.871 | 2022-10-06 | 31.0868 | 7.2158 | 18.4755 | -5.3955 | 2 | PowerSafe | SBS EON 1800 | 32.832 | 8.961 | 9 | 240 | 180 | 156.129 | 77 |  | 1 | 6.2158 | -6.3955 | 19.995 | -34.6161 | 7.961 | 24.2477 | 180 | 23.871 | 156.129 | 1 | 155.129 | 86.1828 |  | Single | SBS EON 1800 | 0 | 0 | 0 | 0 | 0 | SBS EON 1800
WKGN01;DC SYS01 | SOUTH | WOKING | GIS Migrated | WKGN01 | Eaton Powerware APR48-ES | 36.6 | 35 | 135 | 7.3575 | 2022-01-28 | 54.2558 | 46.8983 | 35.1198 | 27.7623 | 3 | PowerSafe | DDm125-33 | 53.3304 | 45.9729 | 5 | 88 | 66 | 58.6425 | 34 |  | 2.4 | 44.4983 | 25.3623 | 82.0158 | 72.2165 | 43.5729 | 81.7037 | 66 | 7.3575 | 58.6425 | 2.4 | 56.2425 | 85.2159 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
WONTL1; DC SYS02 | NORTH WEST | WORKINGTON | Capped | WONTL1 | Eaton Powerware APR48-3G | 37.5 | 6 | 0 | 0 | 2024-03-05 | 8.175 | 8.175 | 8.1096 | 8.1096 | 3 | Enersys | 12V155F | 4.212 | 4.212 | 1 | 8 | 6 | 6 | 1 | Space; Power; Air Con | 0.9 | 7.275 | 7.2096 | 88.9908 | 88.902 | 3.312 | 78.6325 | 6 | 0 | 6 | 0.9 | 5.1 | 85 | Capped | Single | 12V155F | 0 | 0 | 0 | 0 | 0 | 12V155F
WTNTK1;DC SYS01 | NORTH WEST | WARRINGTON | Redstream Optical Network Site | WTNTK1 | Eaton Powerware NPR.48 | 55 | 26 | 691 | 37.6595 | 2022-03-25 16:00 | 59.95 | 22.2905 | 42.2375 | 4.578 | 3 | PowerSafe | DDm125-33 | 53.3304 | 15.6709 | 6 | 94 | 70.5 | 32.8405 | 34 |  | 2.7 | 19.5905 | 1.878 | 32.6781 | 4.4463 | 12.9709 | 24.3218 | 70.5 | 37.6595 | 32.8405 | 2.7 | 30.1405 | 42.7525 |  | Single | DDm125-33 | 0 | RA | 0 | 0 | 0 | DDm125-33
WTT;DC SYS01 | ANGLIA | WINTERTON | Redstream Optical Network Site | WTT | Eaton Powerware APR48-ES | 36.6 | 15 | 137 | 7.4665 | 2021-02-24 | 22.3406 | 14.8741 | 14.8458 | 7.3793 | 2 | PowerSafe | DDm100-25 | 21.1248 | 13.6583 | 5 | 37.8 | 28.35 | 20.8835 | 42 |  | 1 | 13.8741 | 6.3793 | 62.1027 | 42.9704 | 12.6583 | 59.9215 | 28.35 | 7.4665 | 20.8835 | 1 | 19.8835 | 70.1358 |  | Single | DDm100-25 | 0 | 0 | 0 | 0 | 0 | DDm100-25
WVHTF1;DCSys01 | MIDLANDS | WOLVERHAMPTON | GIS Migrated | WVHTF1 | Eaton Powerware APR48-ES | 36.6 | 15 | 178 | 9.701 | 2022-03-07 11:00 | 22.3406 | 12.6396 | 11.2488 | 1.5478 | 3 | PowerSafe | DDm85-25 | 26.1144 | 16.4134 | 3 | 14.8 | 11.1 | 1.399 | 12 |  | 2.4 | 10.2396 | -0.8522 | 45.8341 | -7.5759 | 14.0134 | 53.6616 | 11.1 | 9.701 | 1.399 | 2.4 | -1.001 | -9.018 |  | Single | DDm85-25 | 0 | RA | 0 | 0 | 0 | DDm85-25
YRK;DC SYS01 | NORTH EAST | YORK | Redstream Optical Network Site | YRK | Duvine DD686 | 75 | 9 | 240 | 13.08 | 2020-08-06 | 26.16 | 13.08 | 19.62 | 6.54 | 2 | PowerSafe | DDm100-25 | 21.1248 | 8.0448 | 3 | 44 | 33 | 19.92 | 67 |  | 1 | 12.08 | 5.54 | 46.1774 | 28.2365 | 7.0448 | 33.3485 | 33 | 13.08 | 19.92 | 1 | 18.92 | 57.3333 |  | Single | DDm100-25 | 0 | 0 | 0 | 0 | 0 | DDm100-25
YRKTH1; DC SYS01 | NORTH EAST | YORK | Redstream Optical Network Site | YRKTH1 | Power One PMP 25.48 V3.0 | 50 | 5 | 81.8 | 4.4581 | 2022-06-27 09:52 | 8.72 | 4.2619 | 4.4145 | -0.0436 | 2 | PowerSafe | 2DDm85-15 | 10.1088 | 5.6507 | 2 | 30 | 22.5 | 18.0419 | 42 |  | 0 | 4.2619 | -0.0436 | 48.875 | -0.98765 | 5.6507 | 55.8988 | 22.5 | 4.4581 | 18.0419 | 0 | 18.0419 | 80.1862 |  | Single | 2DDm85-15 | 0 | 0 | 0 | 0 | 0 | 2DDm85-15
| LONDON | CROYDON | Redstream Optical Network Site | CYNTN2 | [15 empty] | 2 | 30 | 22.5 | 18.0419 | 42 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.5 | 0 | 22.5 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| LONDON | VAUXHALL | Redstream Optical Network Site | VHXINT | [15 empty] | 3 | 232 | 174 | 174 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 174 | 0 | 174 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| MIDLANDS | BIRMINGHAM | Redstream Optical Network Site | BSHN08 | [15 empty] | 2 | 30 | 22.5 | 22.5 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.5 | 0 | 22.5 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| MIDLANDS | LEICESTER | Redstream Optical Network Site | LCT EXT (1st Floor) | [15 empty] | 2 | 10.25 | 7.6875 | 7.6875 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.6875 | 0 | 7.6875 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| NORTH EAST | LEEDS | Capped | TGY | [15 empty] | 6 | 55 | 41.25 | 41.25 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 41.25 | 0 | 41.25 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| NORTH EAST | LEEDS | Capped | TGY | [15 empty] | 3 | 15 | 11.25 | 11.25 | 0 | Space | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.25 | 0 | 11.25 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| NORTH EAST | LEEDS | Capped | TGYN03 | [15 empty] | 3 | 64 | 48 | 48 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48 | 0 | 48 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| NORTH EAST | LEEDS | Redstream Optical Network Site | LDSN15 | [15 empty] | 4 | 9 | 6.75 | 6.75 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.75 | 0 | 6.75 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| NORTHERN IRELAND | BALLYWATER | Redstream Optical Network Site | BYR[cabin] | [15 empty] | 0 | 0 |  |  | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SCOTLAND | ABERDEEN | Redstream Optical Network Site | 0 | [15 empty] | 0 | 0 | 0 | 0 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SCOTLAND | AUCHTERAW | Redstream Optical Network Site | FTATA1 | [15 empty] | 2 | 10 | 7.5 | 7.5 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.5 | 0 | 7.5 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SCOTLAND | EDINBURGH | Redstream Optical Network Site | EDBCD1 | [15 empty] | 0 | 0 |  |  | 210 | Audit | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SCOTLAND | FALKIRK | Redstream Optical Network Site | FKKB21 | [15 empty] | 10 | 90 | 67.5 | 67.5 | 2 | Space | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 67.5 | 0 | 67.5 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SOUTH WEST | BRISTOL | Capped | AZTCD2 | [15 empty] | 12 | 594 | 445.5 | 445.5 | 9 | Space | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 445.5 | 0 | 445.5 | #N/A | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0
| SOUTH WEST | SWINDON | Capped | SDNN11 | [15 empty] | 12 | 594 | 445.5 | 445.5 | 9 | Space | [16 empty] | 0 | 0 | 0 | 0
Note on AP7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Trims data in BA to remove extra spaces at end

## Single_Check
Single DC Power System Capacity and Autonomy Checker
System : | YRKTH1; DC SYS01 | Select rectifier module type from drop down list
Rect Type : | Power One PMP 25.48 V3.0 | Select rectifier module type from drop down list
Qty of Rect Fitted : | 5 | Enter number of rectifier module fitted to the system
Existing Load (Amps) : | 81.8 | Enter desired system load, this can be existing load or existing load plus any new requirement
Allocated load (Amps) : | 0 | Enter power requirements for new kit required (leave blank if not required)
Future Kit (Amps): |  | Enter power requirements for future required (leave blank if not required)
System Load Amps : | 81.8 | Auto calculated
System Load (kW) : | 4.4581 | Auto calculated
Battery Strings Fitted : | 2 | Enter number of battery strings fitted to the system
Battery Type : | 2DDm85-15 | Select battery type from drop down list
Battery Recharge Required : | 119 | Auto calculated
Required Load inc Full Battery Recharge (Amps) : | 200.8 | Auto calculated
| Available Rectifier Load Capacity (inc full batt recharge) | Available Rectifier Load Capacity @ 80% of N | Additional Rect Required | Additional Rect Required @ 80% of N
Amps : | 81 | 160 | -1 | -2
kW : | 4.4145 | 8.72
| Capacity Remaining | Capacity Remaining @ 80% of N |  |  | syste
Percentage : | -0.9877% |  | 90% Capacity limit exceeded if cell is red, additional build required
Amps : | -0.8 | 78.2
kW : | -0.0436 | 4.2619
Allowing for 10% for aging
Time (Hours) : | 1 hr | 2 hrs | 3 hrs | 4 hrs
Amps : | 450.2312 | 302.0037 | 229.8716 | 188.6532
kW : | 24.5376 | 16.4592 | 12.528 | 10.2816
Allowing 20% for aging
Time (Hours) : | 1 hr | 2 hrs | 3 hrs | 4 hrs
Amps : | 400.2055 | 268.4477 | 204.3303 | 167.6917
kW : | 21.8112 | 14.6304 | 11.136 | 9.1392

## Space
Equipment Area Code | Available Suite Sections | Allocated | Updated
ABH | 23 | 0 | 23
ABN | 3 | 0 | 3
ABNTB1 | 13 | 0 | 13
ABNTD1 | 0 | 0 | 0
ACTN01 | 178 | 0 | 178
ANSTW1 | 5 | 0 | 5
ASH | 13 | 0 | 13
ASMN02 | 23 | 0 | 23
AYRN01 | 12 | 0 | 12
AZTCD1 | 29 | 0 | 29
BCT | 19 | 0 | 19
BDEN02 | 12 | 0 | 12
BDEN06 | 31 | 0 | 31
BDFN02 | 38 | 0 | 38
BFDTB1 | 96 | 0 | 96
BFEC01 | 12 | 0 | 12
BFTN03 | 19 | 0 | 19
BHMN07 | 0 | 0 | 0
BHMN05 | 5 | 0 | 5
BHMN05 | 5 | 0 | 5
BHMTF1 | 12 | 0 | 12
BHMTF1 | 12 | 0 | 12
BHWCN1 | 0 | 0 | 0
BIFTS1 | 0 | 0 | 0
BKBN41 | 20 | 0 | 20
#REF! | #REF! | 0 | #REF!
BKLN05 | 104 | 0 | 104
BKLN05 | 104 | 0 | 104
BKLN05 | 104 | 0 | 104
BMGV03 | 30 | 0 | 30
BMGV03 | 30 | 0 | 30
BMTDN1 | 2 | 0 | 2
BPL | 6 | 0 | 6
BRETS1 | 9 | 0 | 9
#REF! | #REF! | 0 | #REF!
BRRTS1 | 1 | 0 | 1
BSG | 57 | 0 | 57
BSHN07 | 31 | 0 | 31
BSHN07 | 31 | 0 | 31
BSHN07 | 31 | 0 | 31
BSHN03 | 130 | 0 | 130
BTFTB1 | 18 | 0 | 18
BTFTB1 | 18 | 0 | 18
BTLCD1 | 45 | 0 | 45
BTLN08 | 14 | 0 | 14
BTLN09 | 20 | 0 | 20
BTN | 59 | 0 | 59
BTNW01 | 1 | 0 | 1
BTRTP1 | 3 | 0 | 3
BYR | 4 | 0 | 4
CAMN02 | 1 | 0 | 1
CAMN41 | 12 | 0 | 12
CBY | 13 | 0 | 13
CDFN02 | 15 | 0 | 15
CELL01 | 8 | 0 | 8
CFDTN1 | 6 | 0 | 6
CHDCD1 | 0 | 0 | 0
CHMN21 | 25 | 0 | 25
CHTN07 | 18 | 0 | 18
CHTN07 | 18 | 0 | 18
CHTTN3 | 65 | 0 | 65
CKNN03 | 24 | 0 | 24
CKNN03 | 24 | 0 | 24
COV | 17 | 0 | 17
COWL02 | 7 | 0 | 7
CSLN13 | 8 | 0 | 8
CTNN01 | 20 | 0 | 20
CTNN01 | 20 | 0 | 20
CTRTK1 | 7 | 0 | 7
CTRTS1 | 51 | 0 | 51
CYNTN2(EXT'N) | 6 | 0 | 6
DBY | 18 | 0 | 18
DCT | 11 | 0 | 11
DFSN01 | 47 | 0 | 47
DFSNC1 | 0 | 0 | 0
DGS | 3 | 0 | 3
DHMNU1 | 1 | 0 | 1
DKTN08 | 33 | 0 | 33
DLD | 11 | 0 | 11
DLNTC1 | 67 | 0 | 67
DNDN71 | 17 | 0 | 17
DNDTC1 | 0 | 0 | 0
DNFNP1 | 2 | 0 | 2
DONTN1 | 4 | 0 | 4
DVSTB1 | 14 | 0 | 14
DWLTM1 | 0 | 0 | 0
EBCTC1 | 3 | 0 | 3
EDBN07 | 0 | 0 | 0
EDBTG1 | 4 | 0 | 4
EDBTG1 | 4 | 0 | 4
EDBTN1 | 31 | 0 | 31
EDBTN1 | 31 | 0 | 31
EGNTM1 | 3 | 0 | 3
EVMN01 | 19 | 0 | 19
EXR | 71 | 0 | 71
EXR | 71 | 0 | 71
FKE | 19 | 0 | 19
FLNTT1 | 6 | 0 | 6
FMYN31 | 21 | 0 | 21
FRNN03 | 22 | 0 | 22
FRNN03 | 22 | 0 | 22
GCRTB1 | 24 | 0 | 24
GFDCD1 | 60 | 0 | 60
GLWN07 | 51 | 0 | 51
GLWN07 | 51 | 0 | 51
GLWTO1 | 61 | 0 | 61
GLWTW1 | 3 | 0 | 3
GRSTB1 | 6 | 0 | 6
GWK | 3 | 0 | 3
HHD | 16 | 0 | 16
HLDA11 | 12 | 0 | 12
HLDA12 | 4 | 0 | 4
HLWN02 | 38 | 0 | 38
HRWN02 | 235 | 0 | 235
HTE | 4 | 0 | 4
IGNN01 | 119 | 0 | 119
INVN41 | 29 | 0 | 29
INVTL1 | 1 | 0 | 1
IODN01 | 16 | 0 | 16
IPWTN1 | 98 | 0 | 98
IVER02 | 4 | 0 | 4
KLNN01 | 1 | 0 | 1
KNLTS1 | 4 | 0 | 4
LCT | 11 | 0 | 11
LDMS13 | 4 | 0 | 4
LDMS13 | 4 | 0 | 4
LDSCD2 | 37 | 0 | 37
LDSCD2 | 37 | 0 | 37
LDSN14 | 3 | 0 | 3
LDSTS1 | 135 | 0 | 135
LIVN01 | 44 | 0 | 44
LLDTE1 | 174 | 0 | 174
LMSCN2 | 1 | 0 | 1
LPLTB1 | 4 | 0 | 4
LPLTK1 | 18 | 0 | 18
LSWN01 | 45 | 0 | 45
LTNDN1 | 7 | 0 | 7
MCRCD2 | 55 | 0 | 55
MCRCD2 | 55 | 0 | 55
MCRCD2 | 55 | 0 | 55
MCRN11 | 39 | 0 | 39
MCRN11 | 39 | 0 | 39
MCRN12 | 94 | 0 | 94
MCRN12 | 94 | 0 | 94
MDBTD1 | 27 | 0 | 27
MDE | 17 | 0 | 17
MDFTB1 | 2 | 0 | 2
MKSTN1 | 24 | 0 | 24
NBYCD1 | 0 | 0 | 0
NECCD1 | 0 | 0 | 0
NGM | 21 | 0 | 21
NGMTL1 | 96 | 0 | 96
NRWN51 | 8 | 0 | 8
NRWTN1 | 9 | 0 | 9
NULTB1 | 6 | 0 | 6
NWCN05 | 40 | 0 | 40
NWCNY1 | 24 | 0 | 24
NWPDN1 | 3 | 0 | 3
OHB | 31 | 0 | 31
OHB | 31 | 0 | 31
OKNN01 | 7 | 0 | 7
OKNN01 | 7 | 0 | 7
PCOTN1 | 66 | 0 | 66
PCOTN1 | 66 | 0 | 66
PCOTN1 | 66 | 0 | 66
PCOTN1 | 66 | 0 | 66
PLY | 49 | 0 | 49
PLY | 49 | 0 | 49
PNRTN1 | 8 | 0 | 8
POLN02 | 25 | 0 | 25
POLN02 | 25 | 0 | 25
PRDTB1 | 7 | 0 | 7
PRLN02 | 5 | 0 | 5
PTBTN1 | 9 | 0 | 9
PTHTL1 | 3 | 0 | 3
PTMDN1 | 1 | 0 | 1
PTMN03 | 278 | 0 | 278
RATE02 | 3 | 0 | 3
RATE02 | 3 | 0 | 3
RCR | 17 | 0 | 17
RDG | 27 | 0 | 27
RFDN11 | 35 | 0 | 35
SBHN01 | 84 | 0 | 84
SDN | 6 | 0 | 6
SDNN06 | 61 | 0 | 61
SDNN06 | 61 | 0 | 61
SDNN06 | 61 | 0 | 61
SDNN13 | 4 | 0 | 4
SHD | 6 | 0 | 6
SHDTR1 | 21 | 0 | 21
SHTN03 | 69 | 0 | 69
SLO | 13 | 0 | 13
SMHN02 | 3 | 0 | 3
SNDTM1 | 9 | 0 | 9
SOLN02 | 38 | 0 | 38
SOSTN1 | 30 | 0 | 30
SOT | 22 | 0 | 22
SQYN01 | 104 | 0 | 104
SQYN01 | 104 | 0 | 104
SQYN01 | 104 | 0 | 104
SQYN02 | 94 | 0 | 94
SQYN02 | 94 | 0 | 94
SQYN02 | 94 | 0 | 94
SQYN02 | 94 | 0 | 94
STEDN1 | 1 | 0 | 1
STGCD1 | 13 | 0 | 13
SWNN03 | 5 | 0 | 5
SWY | 13 | 0 | 13
TELHS1 | 2 | 0 | 2
TELHS1 | 2 | 0 | 2
TELHS1 | 2 | 0 | 2
TELHS1 | 2 | 0 | 2
TELHS2 | 0 | 0 | 0
TGYN04 | 6 | 0 | 6
TGYN04 | 6 | 0 | 6
TNTTN1 | 55 | 0 | 55
TNTTN1 | 55 | 0 | 55
TRON01 | 65 | 0 | 65
VHXN02 | 1 | 0 | 1
WADN01 | 8 | 0 | 8
WAHP06 | 9 | 0 | 9
WAHP03 | 64 | 0 | 64
#REF! | #REF! | 0 | #REF!
WAHP03 | 64 | 0 | 64
WAIP06 | 6 | 0 | 6
WCKTR1 | 5 | 0 | 5
WHD | 1 | 0 | 1
WHHN03 | 77 | 0 | 77
WKGN01 | 34 | 0 | 34
WONTL1 | 1 | 0 | 1
#REF! | #REF! | 0 | #REF!
WTNTK1 | 34 | 0 | 34
WTT | 42 | 0 | 42
WVHTF1 | 12 | 0 | 12
YRK | 67 | 0 | 67
YRKTH1 | 42 | 0 | 42
#REF! | #REF! | 0 | #REF!
CYNTN2 | 42 | 0 | 42
VHXINT | 5 | 0 | 5
BSHN08 | 16 | 0 | 16
LCT EXT (1st Floor) | 1 | 0 | 1
TGY | 0 | 0 | 0
TGY | 0 | 0 | 0
TGYN03 | 0 | 0 | 0
LDSN15 | 3 | 0 | 3
BYR[cabin] | 0 | 0 | 0
0 | 1 | 0 | 1
FTATA1 | 0 | 0 | 0
EDBCD1 | 210 | 0 | 210
FKKB21 | 2 | 0 | 2
AZTCD2 | 9 | 0 | 9
#REF! | #REF! | 0 | #REF!
#REF! | #REF! | 0 | #REF!
#REF! | #REF! | 0 | #REF!
SDNN11 | 9 | 0 | 9
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0

## Issue Log
Site | Issue | Date raised | Resolution

## Data
Site | Sites with dual systems | System A | System B | Single systems
ABH | ACTN01 | ACTN01;DC SYS01a | ACTN01;DC SYS01b | ABH;DC SYS01
ABN | BDFN02 | BDFN02;DC SYS01a | BDFN02;DC SYS01b | ABN;DC SYS01
ABNTB1 | BHMN05 | BHMN05;DC SYS A | BHMN05;DC SYS B | ABNTB1;DC SYS01
ABNTD1 | BHMN08 | BHMN08;DCSYS03A | BHMN08;DCSYS03B | ABNTD1;DCSYS01
ACTN01 | BHMTF1 | BHMTF1;DC SYS A | BHMTF1;DC SYS B | ANSTW1; DC SYS01
ANSTW1 | BKLN05 | BKLN05;DC SYS04a | BKLN05;DC SYS04b | ASH;DC SYS01
ASH | BMGV03 | BMGV03; DC SYS A | BMGV03; DC SYS B | ASMN02;DC SYS01
ASMN02 | CHTTN3 | CHTTN3;DC SYS01A | CHTTN3;DC SYS01B | AYRN01; DC SYS01
AYRN01 | CKNN03 | CKNN03-DCSYS01a | CKNN03-DCSYS01b | AZTCD1&2;DC SYS01
AZTCD1 | COV | COV;DC SYS01a | COV;DC SYS01b | BCT;DC SYS01
BCT | CTTN01 | CTNN01-DCSYS01a | CTNN01-DCSYS01b | BDEN02;DC SYS01
BDEN02 | EDBTG1 | EDBTG1;DC SYSA | EDBTG1;DC SYSB | BDEN06;DC SYS01
BDEN06 | EDBTN1 | EDBTN1;DC SYSA (DO NOT CONNECT LOADS) | EDBTN1;DC SYSB | BFDTB1;DC SYS01
BDFN02 | EXRN03 | EXRN03-DCSYS01a | EXRN03-DCSYS01b | BFEC01;DC SYS01
BFDTB1 | FRNN03 | FRNN03-DCSYS01a | FRNN03-DCSYS01b | BFTN03;DC SYS01
BFEC01 | GFDCD1 | GFDCD1;DC SYS01A | GFDCD1;DC SYS01B | BHM;DC SYS02
BFTN03 | GLWN07 | GLWN07;DC SYS A | GLWN07;DC SYS B | BHWCN1;DC SYS01
BHMN07 | LDMS13 | LDMS13;DC SYS01 A | LDMS13;DC SYS01 B | BIFTS1; DC SYS01
BHMN05 | LDSCD2 | LDSCD2;DC SYS A | LDSCD2;DC SYS B | BKBN41;DC SYS01
BHMN08 | MCRN11 | MCRN11;DC SYS01a | MCRN11;DC SYS01b | BKLN05;DC SYS02
BHMTF1 | MCRN12 | MCRN12;DC SYS01 A | MCRN12;DC SYS01 B | BKLN05;DC SYS03;NEAR CK
BHWCN1 | NWCN05 | NWCN05;DC SYS01a | NWCN05;DC SYS01b | BMTDN1;DC SYS01
BIFTS1 | OKNN01 | OKNN01-DCSYS01a | OKNN01-DCSYS01b | BPL;DC SYS01
BKBN41 | PCOTN1_Flag | PCOTN1;DC SYS A;FLAG | PCOTN1;DC SYS B;FLAG | BRETS1;DC SYS01
BKLN05 | PCOTN1_Gemini | PCOTN1;DC SYS A;GEMINI | PCOTN1;DC SYS B;GEMINI | BRN;DC SYS01
BKLN05 Ext | PLY | PLY-DCSYS01a | PLY-DCSYS01b | BRRTS1; DC SYS01
BMGV03 | POLN02 | POLN02-DCSYS01a | POLN02-DCSYS01b | BSG;DC SYS01
BMTDN1 | RATE02 | RATE02;DC SYS01 | RATE02;DC SYS02 | BSH;DC SYS01;GND
BPL | SQYN02 - SYS8 | SQYN02;DC SYS08A | SQYN02;DC SYS08B | BSH;DC SYS02;GND
BRETS1 | SQYN02 - SYS9 | SQYN02;DC SYS09a | SQYN02;DC SYS09b | BSH;DC SYS03;GND
BRRTS1 | TGY | TGY;DC SYSA | TGY;DC SYSB **DO NOT CONNECT LOADS** | BSHN03;DC SYS A
BSG | TNTTN1 | TNTTN1-DCSYS01a | TNTTN1-DCSYS01b | BSHN03;DC SYS B
BSHN07 | WAHP06 | WAHP; DC SYS A (Feeds WAHP06) | WAHP; DC SYS B (Feeds WAHP06) | BTFTB1;DC SYS01
BSHN03 | WAHP03 | WAHP;DC SYS A Tx | WAHP;DC SYS B Tx | BTFTB1;DC SYS02
BTFTB1 |  |  |  | BTLCD1;DC SYS01
BTLCD1 |  |  |  | BTLN08;DC SYS01
BTLN08 |  |  |  | BTLN09;DC SYS01
BTLN09 |  |  |  | BTN-DCSYS01
BTN |  |  |  | BTNW01;DC SYS01
BTNW01 |  |  |  | BTRTP1;DC SYS01
BTRTP1 |  |  |  | BYR;DC SYS01
BYR |  |  |  | CAMN02;DC SYS01
CAMN02 |  |  |  | CAMN41;DC SYS01
CAMN41 |  |  |  | CBY;DC SYS01
CBY |  |  |  | CDFN02;DC SYS01
CDFN02 |  |  |  | CELL01;DC SYS01
CELL01 |  |  |  | CFDTN1;DC SYS01
CFDTN1 |  |  |  | CHDCD1;DC SYS01
CHDCD1 |  |  |  | CHMN21;DC SYS01
CHMN21 |  |  |  | CHTN07;DC SYS01
CHTN07 |  |  |  | CHTN07;DC SYS02
CHTTN3 |  |  |  | COWL02;DC SYS01
CKNN03 |  |  |  | CSLN13;DC SYS01
COV |  |  |  | CTRTK1;DC SYS01
COWL02 |  |  |  | CTRTS1; DC SYS01
CSLN13 |  |  |  | CYNTN2;DC SYS01
CTNN01 |  |  |  | DBY;DC SYS01
CTRTK1 |  |  |  | DCT;DC SYS01
CTRTS1 |  |  |  | DFSN01; DC SYS01
CYNTN2(EXT'N) |  |  |  | DFSNC1; DC SYS01
DBY |  |  |  | DGS;DC SYS01
DCT |  |  |  | DHMNU1;DC SYS01
DFSN01 |  |  |  | DKTN08; DC SYS01
DFSNC1 |  |  |  | DLD;DC SYS01
DGS |  |  |  | DLNTC1;DC SYS01
DHMNU1 |  |  |  | DNDN71; SYS 01
DKTN08 |  |  |  | DNDTC1;DCSYS01
DLD |  |  |  | DNFNP1; DC SYS01
DLNTC1 |  |  |  | DONTN1;DC SYS01
DNDN71 |  |  |  | DVSTB1; DC SYS01
DNDTC1 |  |  |  | DWLTM1;DC SYS01
DNFNP1 |  |  |  | ECBTC1; DC SYS01
DONTN1 |  |  |  | EDBCD1;DC SYS01
DVSTB1 |  |  |  | EGNTM1;DC SYS01
DWLTM1 |  |  |  | EVMN01;DC SYS01
EBCTC1 |  |  |  | EXR;DC SYS01
EDBN07 |  |  |  | FKE;DC SYS01
EDBTG1 |  |  |  | FLNTT1;DC SYS01
EDBTN1 |  |  |  | FMYN31; DC SYS01
EGNTM1 |  |  |  | GCRTB1;DC SYS01
EVMN01 |  |  |  | GLWTO1;DC SYS01
EXR |  |  |  | GLWTW1;DC SYS01
FKE |  |  |  | GRSTB1;DC SYS01
FLNTT1 |  |  |  | GWK;DC SYS01
FMYN31 |  |  |  | HHD;DC SYS01
FRNN03 |  |  |  | HLDA11;DC SYS01
GCRTB1 |  |  |  | HLDA12;DC SYS01
GFDCD1 |  |  |  | HLWN02;DC SYS01
GLWN07 |  |  |  | HRWN02;DC SYS01
GLWTO1 |  |  |  | HTE;DC SYS01
GLWTW1 |  |  |  | IGNN01;DC SYS01
GRSTB1 |  |  |  | INVN41;DC SYS01
GWK |  |  |  | INVTL1;DC SYS01
HHD |  |  |  | IODN01;DC SYS01
HLDA11 |  |  |  | IODTA1;DC SYS01
HLDA12 |  |  |  | IPWTN1;DC SYS01
HLWN02 |  |  |  | IVER02; DC SYS01
HRWN02 |  |  |  | KLNN01;DC SYS01
HTE |  |  |  | KNLTS1;DC SYS01
IGNN01 |  |  |  | LCT;DC SYS01
INVN41 |  |  |  | LDSN14; DC SYS01
INVTL1 |  |  |  | LDSTS1;DC SYS01
IODN01 |  |  |  | LIVN01;DC SYS01
IODTA1 |  |  |  | LLDTE1;DC SYS01
IPWTN1 |  |  |  | LMSCN2;DC SYS01
IVER02 |  |  |  | LPLTB1;DC SYS01
KLNN01 |  |  |  | LPLTK1;DC SYS01
KNLTS1 |  |  |  | LSWN01;DC SYS01
LCT |  |  |  | LTNDN1;DC SYS01
LDMS13 |  |  |  | MCRCD2;DC SYS01 [Rect1&2]
LDSCD2 |  |  |  | MCRCD2;DC SYS02 [Rect 3&4]
LDSN14 |  |  |  | MCRCD2;DC SYS03 [Rect5] (Decommissioned)
LDSTS1 |  |  |  | MDBTD1;DC SYS01
LIVN01 |  |  |  | MDE;DC SYS01
LLDTE1 |  |  |  | MDFTB1;DC SYS01
LMSCN2 |  |  |  | MKSTN1;DC SYS01
LPLTB1 |  |  |  | NBYCD1;DC SYS01
LPLTK1 |  |  |  | NECCD1;DC SYS01
LSWN01 |  |  |  | NGM;DC SYS03
LTNDN1 |  |  |  | NGMTL1;DC SYS01
MCRCD2 |  |  |  | NRWN51;DC SYS01
MCRN11 |  |  |  | NRWTN1;DC SYS01
MCRN12 |  |  |  | NULTB1;DC SYS01
MDBTD1 |  |  |  | NWCNY1;DC SYS01
MDE |  |  |  | NWPDN1;DC SYS01
MDFTB1 |  |  |  | OHB;DC SYS01;PSU1
MKSTN1 |  |  |  | OHB;DC SYS02;PSU2
NBYCD1 |  |  |  | PNRTN1;DC SYS01
NECCD1 |  |  |  | PRDTB1;DC SYS01
NGM |  |  |  | PRLN02;DC SYS01
NGMTL1 |  |  |  | PTBTN1;DC SYS01
NRWN51 |  |  |  | PTHTL1;DC SYS01
NRWTN1 |  |  |  | PTMDN1;DC SYS01
NULTB1 |  |  |  | PTMN03;DC SYS01
NWCN05 |  |  |  | RCR;DC SYS01
NWCNY1 |  |  |  | RDGCD2;DC SYS01
NWPDN1 |  |  |  | RDG;DC SYS01
OHB |  |  |  | RFDN11;DC SYS01
OKNN01 |  |  |  | SBHN01;DC SYS01
PCOTN1 |  |  |  | SDN;DC SYS01
PLY |  |  |  | SDNN06;DC SYS02
PNRTN1 |  |  |  | SDNN06;DC SYS03
POLN02 |  |  |  | SDNN11;DC SYS01
PRDTB1 |  |  |  | SDNN13;DC SYS01
PRLN02 |  |  |  | SHD;DC SYS01
PTBTN1 |  |  |  | SHDTR1;DC SYS01
PTHTL1 |  |  |  | SHTN03;DC SYS02
PTMDN1 |  |  |  | SLO;DC SYS01
PTMN03 |  |  |  | SMHN02;DC SYS01
RATE02 |  |  |  | SNDTM1;DC SYS01
RCR |  |  |  | SOL;DC SYS01
RDGCD2 |  |  |  | SOSTN1;DC SYS01
RDG |  |  |  | SOT;DC SYS01
RFDN11 |  |  |  | SQYN01;DC SYS01
SBHN01 |  |  |  | SQYN01;DC SYS02
SDN |  |  |  | SQYN01;DC SYS03
SDNN06 |  |  |  | STEDN1;DC SYS01
SDNN13 |  |  |  | STGCD1;DC SYS01
SHD |  |  |  | SWNN03;DC SYS01
SHDTR1 |  |  |  | SWY;DC SYS01
SHTN03 |  |  |  | TELHS1;DC SYS A;EXT ROOM
SLO |  |  |  | TELHS1;DC SYS B;EXT ROOM
SMHN02 |  |  |  | TELHS1;SYS;A;DC PER02;9D
SNDTM1 |  |  |  | TELHS1;SYS;B;DC PER03;1L
SOLN02 |  |  |  | TELHS2;DC SYS01
SOSTN1 |  |  |  | THOTC1;DC SYS01
SOT |  |  |  | TRON01;DC SYS01
SQYN01 |  |  |  | VHXN02;DC SYS01
SQYN02 |  |  |  | WADN01;DC SYS01
STEDN1 |  |  |  | WAIP;DC SYS01;GND
STGCD1 |  |  |  | WCKTR1;DCSYS01
SWNN03 |  |  |  | WHD;DC SYS01
SWY |  |  |  | WHHN03;DC SYS01
TELHS1 |  |  |  | WKGN01;DC SYS01
TELHS2 |  |  |  | WONTL1; DC SYS02
TGYN04 |  |  |  | WTNTK1;DC SYS01
THOTC1 |  |  |  | WTT;DC SYS01
TNTTN1 |  |  |  | WVHTF1;DCSys01
TRON01 |  |  |  | YRK;DC SYS01
VHXN02 |  |  |  | YRKTH1; DC SYS01
WADN01
WAHP06
WAHP03
WAIP06
WCKTR1
WHD
WHHN03
WKGN01
WONTL1
WTNTK1
WTT
WVHTF1
YRK
YRKTH1
CYNTN2
VHXINT
BSHN08
LCT EXT (1st Floor)
TGY
TGYN03
LDSN15
BYR[cabin]
0
FTATA1
EDBCD1
FKKB21
Note on A1: Frost, Daniel, Vodafone UK: To make site check drop down unique values

## Rectifier_Lookup
Rectifier Model | Output (Amps) | 80% N
Advance MRF2800 | 50 | 40
Advance TRE 1500 | 31.3 | 25.04
Advance TRE 2100 | 43.8 | 35.04
Benning Tebechop 2700 | 50 | 40
Duvine DD686 | 75 | 60
Eaton APR48 | 30 | 24
Eaton APR48-3G | 37.5 | 30
Eaton Powerware APR48-ES | 36.6 | 29.28
Eaton Powerware NPR.48 | 55 | 44
Eaton R2948 | 60 | 48
Eltek Flatpack 1500 | 29.1 | 23.28
Eltek Flatpack2 - 1800 | 37.5 | 30
Power One PMP 10.48 SIC | 22 | 17.6
Power One PMP 11.48 | 23 | 18.4
Power One PMP 13.48 | 28 | 22.4
Power One PMP 16.48 | 32 | 25.6
Power One PMP 25.48 | 45 | 36
Power One PMP 25.48 V3.0 | 50 | 40
Switchtec E1333 | 25 | 20
Switchtec E2733 | 50 | 40
Benning Tebechop 15000 48-225 | 225 | 180
Nortel Helios 100 | 100 | 80
Eaton Powerware HDR48-ES | 55 | 44

## Battery_Lookup_10%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Constant Power | Watts/Cell to 1.8VPC |  |  |  | Amps / String (allow 10% aging) |  |  |  | kW / String (allow 10% aging)
Battery Type | 1 hr | 2 hrs | 3 hrs | 4 hrs | 1 hr2 | 2 hrs3 | 3 hrs4 | 4 hrs5 | 1 hr6 | 2 hrs7 | 3 hrs8 | 4 hrs9 | Ah Rating | Recharge | Temp
2DDm50-09 | 208 | 134 | 100 | 82 | 82.4367 | 53.1083 | 39.633 | 32.4991 | 4.4928 | 2.8944 | 2.16 | 1.7712 | 200 | 20 | 25
2DDm50-13 | 312 | 201 | 151 | 123 | 123.655 | 79.6624 | 59.8459 | 48.7486 | 6.7392 | 4.3416 | 3.2616 | 2.6568 | 300 | 30 | 25
DDm50-17 | 417 | 268 | 201 | 164 | 165.2697 | 106.2165 | 79.6624 | 64.9982 | 9.0072 | 5.7888 | 4.3416 | 3.5424 | 400 | 40 | 25
2DDm85-13 | 487 | 327 | 248 | 204 | 193.0128 | 129.6 | 98.2899 | 80.8514 | 10.5192 | 7.0632 | 5.3568 | 4.4064 | 510 | 51 | 25
2DDm85-15 | 568 | 381 | 290 | 238 | 225.1156 | 151.0018 | 114.9358 | 94.3266 | 12.2688 | 8.2296 | 6.264 | 5.1408 | 595 | 59.5 | 25
DDm85-21 | 812 | 545 | 414 | 340 | 321.8202 | 216 | 164.0807 | 134.7523 | 17.5392 | 11.772 | 8.9424 | 7.344 | 850 | 85 | 25
DDm85-25 | 974 | 654 | 496 | 408 | 386.0257 | 259.2 | 196.5798 | 161.7028 | 21.0384 | 14.1264 | 10.7136 | 8.8128 | 1020 | 102 | 25
DDm85-27 | 1055 | 708 | 538 | 442 | 418.1284 | 280.6018 | 213.2257 | 175.178 | 22.788 | 15.2928 | 11.6208 | 9.5472 | 1105 | 110.5 | 25
DDm85-33 | 1299 | 871 | 662 | 544 | 514.833 | 345.2037 | 262.3706 | 215.6037 | 28.0584 | 18.8136 | 14.2992 | 11.7504 | 1360 | 136 | 25
DDm100-21 | 947 | 640 | 485 | 397 | 375.3248 | 253.6514 | 192.2202 | 157.3431 | 20.4552 | 13.824 | 10.476 | 8.5752 | 1000 | 100 | 25
DDm100-25 | 1136 | 768 | 582 | 476 | 450.2312 | 304.3817 | 230.6642 | 188.6532 | 24.5376 | 16.5888 | 12.5712 | 10.2816 | 1200 | 120 | 25
DDm100-27 | 1231 | 832 | 631 | 516 | 487.8826 | 329.7468 | 250.0844 | 204.5064 | 26.5896 | 17.9712 | 13.6296 | 11.1456 | 1300 | 130 | 25
DDm100-33 | 1514 | 1024 | 777 | 635 | 600.044 | 405.8422 | 307.9486 | 251.6697 | 32.7024 | 22.1184 | 16.7832 | 13.716 | 1600 | 160 | 25
DDm125-25 | 1448 | 969 | 738 | 607 | 573.8862 | 384.044 | 292.4917 | 240.5725 | 31.2768 | 20.9304 | 15.9408 | 13.1112 | 1500 | 150 | 25
DDm125-27 | 1568 | 1050 | 799 | 658 | 621.4459 | 416.1468 | 316.6679 | 260.7853 | 33.8688 | 22.68 | 17.2584 | 14.2128 | 1625 | 162.5 | 25
DDm125-33 | 1930 | 1292 | 984 | 810 | 764.9174 | 512.0587 | 389.989 | 321.0275 | 41.688 | 27.9072 | 21.2544 | 17.496 | 2000 | 200 | 25 | 749.6191 | 734.6267 | 719.9342 | 705.5355 | 691.4248
12V155F | 195.7 | 115 | 82.5 | 65 | 77.5618 | 45.578 | 32.6972 | 25.7615 | 4.2271 | 2.484 | 1.782 | 1.404 | 150 | 15 | 20
12V101F | 126.8 | 71.1 | 51.9 | 41.5 | 50.2547 | 28.1791 | 20.5695 | 16.4477 | 2.7389 | 1.5358 | 1.121 | 0.8964 | 100 | 10 | 20
12V190F | 263.6 | 154.6 | 110.5 | 86.3 | 104.4727 | 61.2727 | 43.7945 | 34.2033 | 5.6938 | 3.3394 | 2.3868 | 1.8641 | 190 | 19 | 20
12V100F | 131 | 79 | 57 | 45 | 51.9193 | 31.3101 | 22.5908 | 17.8349 | 2.8296 | 1.7064 | 1.2312 | 0.972 | 100 | 10 | 20
12V105F | 130 | 78 | 56 | 45 | 51.5229 | 30.9138 | 22.1945 | 17.8349 | 2.808 | 1.6848 | 1.2096 | 0.972 | 105 | 10.5 | 20
12V125F | 145 | 88 | 65 | 52 | 57.4679 | 34.8771 | 25.7615 | 20.6092 | 3.132 | 1.9008 | 1.404 | 1.1232 | 125 | 12.5 | 20
12V92F | 120 | 70 | 50 | 39 | 47.5596 | 27.7431 | 19.8165 | 15.4569 | 2.592 | 1.512 | 1.08 | 0.8424 | 92 | 9.2 | 20
2V500/6 | 632 | 361 | 269 | 214 | 250.4807 | 143.0752 | 106.6128 | 84.8147 | 13.6512 | 7.7976 | 5.8104 | 4.6224 | 516 | 51.6 | 20
SBS 12V100F | 138 | 81 | 58 | 45 | 54.6936 | 32.1028 | 22.9872 | 17.8349 | 2.9808 | 1.7496 | 1.2528 | 0.972 | 100 | 10 | 20
SBS680 | 650.6 | 452.8 | 347.2 | 282.5 | 257.8525 | 179.4583 | 137.6059 | 111.9633 | 14.053 | 9.7805 | 7.4995 | 6.102 | 680 | 68 | 20
SBS480 | 459.2 | 319.6 | 245.1 | 199.4 | 181.9949 | 126.6672 | 97.1406 | 79.0283 | 9.9187 | 6.9034 | 5.2942 | 4.307 | 480 | 48 | 20
SBS XL 150F-FT | 177 | 107 | 79 | 63 | 70.1505 | 42.4073 | 31.3101 | 24.9688 | 3.8232 | 2.3112 | 1.7064 | 1.3608 | 150 | 15 | 20
SBS EON 1800 | 1889 | 1258 | 938 | 760 | 748.6679 | 498.5835 | 371.7578 | 301.211 | 40.8024 | 27.1728 | 20.2608 | 16.416 | 1870 | 187 | 20
SBS XL 170F-FT | 202 | 122 | 89.4 | 71.3 | 80.0587 | 48.3523 | 35.4319 | 28.2583 | 4.3632 | 2.6352 | 1.931 | 1.5401 | 170 | 17 | 20
SBS EON 2700 | 2727 | 1816 | 1355 | 1097 | 1080.7927 | 719.7358 | 537.0275 | 434.7743 | 58.9032 | 39.2256 | 29.268 | 23.6952 | 2700 | 270 | 20
6V165/6 | 210 | 120 | 90 | 71 | 83.2294 | 47.5596 | 35.6697 | 28.1394 | 4.536 | 2.592 | 1.944 | 1.5336 | 165 | 16.5 | 20
SBS C11F | 121 | 71 | 50 | 40 | 47.956 | 28.1394 | 19.8165 | 15.8532 | 2.6136 | 1.5336 | 1.08 | 0.864 | 92 | 9.2 | 20
12UTMB160 | 194 | 112 | 81.9 | 65.6 | 76.8881 | 44.389 | 32.4594 | 25.9993 | 4.1904 | 2.4192 | 1.769 | 1.417 | 160 | 16 | 20
2SLA800 | 890 | 566 | 426 | 343 | 352.7339 | 224.3229 | 168.8367 | 135.9413 | 19.224 | 12.2256 | 9.2016 | 7.4088 | 800 | 80 | 20
2SLA1000 | 1112 | 707 | 532 | 429 | 440.7193 | 280.2055 | 210.8477 | 170.0257 | 24.0192 | 15.2712 | 11.4912 | 9.2664 | 1000 | 100 | 20
2SLA1500 | 1372 | 930 | 708 | 579 | 543.7651 | 368.5872 | 280.6018 | 229.4752 | 29.6352 | 20.088 | 15.2928 | 12.5064 | 1500 | 150 | 20
2SLA2000 | 1830 | 1239 | 944 | 773 | 725.2844 | 491.0532 | 374.1358 | 306.3633 | 39.528 | 26.7624 | 20.3904 | 16.6968 | 2000 | 200 | 20
2CP1000 | 1183 | 721 | 526 | 418 | 468.8587 | 285.7541 | 208.4697 | 165.6661 | 25.5528 | 15.5736 | 11.3616 | 9.0288 | 1000 | 100 | 20
2CP1400 | 1602 | 1009 | 736 | 585 | 634.9211 | 399.8972 | 291.6991 | 231.8532 | 34.6032 | 21.7944 | 15.8976 | 12.636 | 14000 | 1400 | 25
2CP2000 | 2022.5 | 1268.4 | 933 | 741.8 | 801.578 | 502.7053 | 369.7761 | 293.9978 | 43.686 | 27.3974 | 20.1528 | 16.0229 | 2000 | 200
2CP1600 | 1854 | 1173 | 853 | 671 | 734.7963 | 464.8954 | 338.0697 | 265.9376 | 40.0464 | 25.3368 | 18.4248 | 14.4936 | 1600 | 160
2CP3000 | 3066.7 | 1908.9 | 1392.8 | 1106.6 | 1215.4261 | 756.5549 | 552.0088 | 438.5791 | 66.2407 | 41.2322 | 30.0845 | 23.9026 | 3000 | 300
2CP1200 | 1349 | 865 | 631 | 502 | 534.6495 | 342.8257 | 250.0844 | 198.9578 | 29.1384 | 18.684 | 13.6296 | 10.8432 | 1200 | 120
2CP650 | 776 | 472 | 345 | 274 | 307.5523 | 187.0679 | 136.7339 | 108.5945 | 16.7616 | 10.1952 | 7.452 | 5.9184 | 652 | 65.2
VH57 | 1899 | 1200 | 893 | 720 | 752.6312 | 475.5963 | 353.9229 | 285.3578 | 41.0184 | 25.92 | 19.2888 | 15.552 | 1680 | 168
EN480-2 | 591 | 355 | 254 | 203 | 234.2312 | 140.6972 | 100.6679 | 80.455 | 12.7656 | 7.668 | 5.4864 | 4.3848 | 489 | 48.9
EN160-6 | 197 | 118 | 84.8 | 67.5 | 78.0771 | 46.767 | 33.6088 | 26.7523 | 4.2552 | 2.5488 | 1.8317 | 1.458 | 163 | 16.3
EN320-2 | 394 | 237 | 170 | 135 | 156.1541 | 93.9303 | 67.3761 | 53.5046 | 8.5104 | 5.1192 | 3.672 | 2.916 | 260 | 26

## Battery_Lookup_20%
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Constant Power | Watts/Cell to 1.8VPC |  |  |  | Amps / String (allow 20% aging) |  |  |  | kW / String (allow 20% aging)
Battery Type | 1 hr | 2 hrs | 3 hrs | 4 hrs | 1 hr2 | 2 hrs3 | 3 hrs4 | 4 hrs5 | 1 hr6 | 2 hrs7 | 3 hrs8 | 4 hrs9 | Ah Rating | Recharge | Temp
2DDm50-09 | 208 | 134 | 100 | 82 | 73.2771 | 47.2073 | 35.2294 | 28.8881 | 3.9936 | 2.5728 | 1.92 | 1.5744 | 200 | #REF! | #REF!
2DDm50-13 | 312 | 201 | 151 | 123 | 109.9156 | 70.811 | 53.1963 | 43.3321 | 5.9904 | 3.8592 | 2.8992 | 2.3616 | 300 | #REF! | #REF!
DDm50-17 | 417 | 268 | 201 | 164 | 146.9064 | 94.4147 | 70.811 | 57.7761 | 8.0064 | 5.1456 | 3.8592 | 3.1488 | 400 | #REF! | #REF!
2DDm85-13 | 487 | 327 | 248 | 204 | 171.567 | 115.2 | 87.3688 | 71.8679 | 9.3504 | 6.2784 | 4.7616 | 3.9168 | 510 | #REF! | #REF!
2DDm85-15 | 568 | 381 | 290 | 238 | 200.1028 | 134.2239 | 102.1651 | 83.8459 | 10.9056 | 7.3152 | 5.568 | 4.5696 | 595 | #REF! | #REF!
DDm85-21 | 812 | 545 | 414 | 340 | 286.0624 | 192 | 145.8495 | 119.7798 | 15.5904 | 10.464 | 7.9488 | 6.528 | 850 | #REF! | #REF!
DDm85-25 | 974 | 654 | 496 | 408 | 343.1339 | 230.4 | 174.7376 | 143.7358 | 18.7008 | 12.5568 | 9.5232 | 7.8336 | 1020 | #REF! | #REF!
DDm85-27 | 1055 | 708 | 538 | 442 | 371.6697 | 249.4239 | 189.5339 | 155.7138 | 20.256 | 13.5936 | 10.3296 | 8.4864 | 1105 | #REF! | #REF!
DDm85-33 | 1299 | 871 | 662 | 544 | 457.6294 | 306.8477 | 233.2183 | 191.6477 | 24.9408 | 16.7232 | 12.7104 | 10.4448 | 1360 | #REF! | #REF!
DDm100-21 | 947 | 640 | 485 | 397 | 333.622 | 225.4679 | 170.8624 | 139.8606 | 18.1824 | 12.288 | 9.312 | 7.6224 | 1000 | #REF! | #REF!
DDm100-25 | 1136 | 768 | 582 | 476 | 400.2055 | 270.5615 | 205.0349 | 167.6917 | 21.8112 | 14.7456 | 11.1744 | 9.1392 | 1200 | #REF! | #REF!
DDm100-27 | 1231 | 832 | 631 | 516 | 433.6734 | 293.1083 | 222.2972 | 181.7835 | 23.6352 | 15.9744 | 12.1152 | 9.9072 | 1300 | #REF! | #REF!
DDm100-33 | 1514 | 1024 | 777 | 635 | 533.3725 | 360.7486 | 273.7321 | 223.7064 | 29.0688 | 19.6608 | 14.9184 | 12.192 | 1600 | #REF! | #REF!
DDm125-25 | 1448 | 969 | 738 | 607 | 510.1211 | 341.3725 | 259.9927 | 213.8422 | 27.8016 | 18.6048 | 14.1696 | 11.6544 | 1500 | #REF! | #REF!
DDm125-27 | 1568 | 1050 | 799 | 658 | 552.3963 | 369.9083 | 281.4826 | 231.8092 | 30.1056 | 20.16 | 15.3408 | 12.6336 | 1625 | #REF! | #REF!
DDm125-33 | 1930 | 1292 | 984 | 810 | 679.9266 | 455.1633 | 346.6569 | 285.3578 | 37.056 | 24.8064 | 18.8928 | 15.552 | 2000 | #REF! | #REF!
12V155F | 195.7 | 115 | 82.5 | 65 | 68.9439 | 40.5138 | 29.0642 | 22.8991 | 3.7574 | 2.208 | 1.584 | 1.248 | 150 | #REF! | #REF!
12V101F | 126.8 | 71.1 | 51.9 | 41.5 | 44.6708 | 25.0481 | 18.284 | 14.6202 | 2.4346 | 1.3651 | 0.99648 | 0.7968 | 100 | #REF! | #REF!
12V190F | 263.6 | 154.6 | 110.5 | 86.3 | 92.8646 | 54.4646 | 38.9284 | 30.4029 | 5.0611 | 2.9683 | 2.1216 | 1.657 | 190 | #REF! | #REF!
12V100F | 131 | 79 | 57 | 45 | 46.1505 | 27.8312 | 20.0807 | 15.8532 | 2.5152 | 1.5168 | 1.0944 | 0.864 | 100 | #REF! | #REF!
12V105F | 130 | 78 | 56 | 45 | 45.7982 | 27.4789 | 19.7284 | 15.8532 | 2.496 | 1.4976 | 1.0752 | 0.864 | 105 | #REF! | #REF!
12V125F | 145 | 88 | 65 | 52 | 51.0826 | 31.0018 | 22.8991 | 18.3193 | 2.784 | 1.6896 | 1.248 | 0.9984 | 125 | #REF! | #REF!
12V92F | 120 | 70 | 50 | 39 | 42.2752 | 24.6606 | 17.6147 | 13.7394 | 2.304 | 1.344 | 0.96 | 0.7488 | 92 | #REF! | #REF!
2V500/6 | 632 | 361 | 269 | 214 | 222.6495 | 127.178 | 94.767 | 75.3908 | 12.1344 | 6.9312 | 5.1648 | 4.1088 | 516 | #REF! | #REF!
SBS 12V100F | 138 | 81 | 58 | 45 | 48.6165 | 28.5358 | 20.433 | 15.8532 | 2.6496 | 1.5552 | 1.1136 | 0.864 | 100 | #REF! | #REF!
SBS680 | 650.6 | 452.8 | 347.2 | 282.5 | 229.2022 | 159.5185 | 122.3163 | 99.5229 | 12.4915 | 8.6938 | 6.6662 | 5.424 | 680 | #REF! | #REF!
SBS480 | 459.2 | 319.6 | 245.1 | 199.4 | 161.7732 | 112.593 | 86.3472 | 70.2473 | 8.8166 | 6.1363 | 4.7059 | 3.8285 | 480 | #REF! | #REF!
SBS XL 150F-FT | 177 | 107 | 79 | 63 | 62.356 | 37.6954 | 27.8312 | 22.1945 | 3.3984 | 2.0544 | 1.5168 | 1.2096 | 150 | #REF! | #REF!
SBS EON 1800 | 1889 | 1258 | 938 | 760 | 665.4826 | 443.1853 | 330.4514 | 267.7431 | 36.2688 | 24.1536 | 18.0096 | 14.592 | 1870 | #REF! | #REF!
SBS XL 170F-FT | 202 | 122 | 89.4 | 71.3 | 71.1633 | 42.9798 | 31.495 | 25.1185 | 3.8784 | 2.3424 | 1.7165 | 1.369 | 170 | #REF! | #REF!
SBS EON 2700 | 2727 | 1816 | 1355 | 1097 | 960.7046 | 639.7651 | 477.3578 | 386.4661 | 52.3584 | 34.8672 | 26.016 | 21.0624 | 2700 | #REF! | #REF!
6V165/6 | 210 | 120 | 90 | 71 | 73.9817 | 42.2752 | 31.7064 | 25.0128 | 4.032 | 2.304 | 1.728 | 1.3632 | 165 | #REF! | #REF!
SBS C11F | 121 | 71 | 50 | 40 | 42.6275 | 25.0128 | 17.6147 | 14.0917 | 2.3232 | 1.3632 | 0.96 | 0.768 | 92 | #REF! | #REF!
12UTMB160 | 194 | 112 | 81.9 | 65.6 | 68.345 | 39.4569 | 28.8528 | 23.1105 | 3.7248 | 2.1504 | 1.5725 | 1.2595 | 160 | #REF! | #REF!
2SLA800 | 890 | 566 | 426 | 343 | 313.5413 | 199.3982 | 150.0771 | 120.8367 | 17.088 | 10.8672 | 8.1792 | 6.5856 | 800 | #REF! | #REF!
2SLA1000 | 1112 | 707 | 532 | 429 | 391.7505 | 249.0716 | 187.4202 | 151.1339 | 21.3504 | 13.5744 | 10.2144 | 8.2368 | 1000 | #REF! | #REF!
2SLA1500 | 1372 | 930 | 708 | 579 | 483.3468 | 327.633 | 249.4239 | 203.978 | 26.3424 | 17.856 | 13.5936 | 11.1168 | 1500 | #REF! | #REF!
2SLA2000 | 1830 | 1239 | 944 | 773 | 644.6972 | 436.4917 | 332.5651 | 272.3229 | 35.136 | 23.7888 | 18.1248 | 14.8416 | 2000 | #REF! | #REF!
2CP1000 | 1183 | 721 | 526 | 418 | 416.7633 | 254.0037 | 185.3064 | 147.2587 | 22.7136 | 13.8432 | 10.0992 | 8.0256 | 1000 | #REF! | 20
2CP1400 | 1602 | 1009 | 736 | 585 | 564.3743 | 355.4642 | 259.2881 | 206.0917 | 30.7584 | 19.3728 | 14.1312 | 11.232 | 14000 | #REF! | #REF!
2CP2000 | 2022.5 | 1268.4 | 933 | 741.8 | 712.5138 | 446.8492 | 328.6899 | 261.3314 | 38.832 | 24.3533 | 17.9136 | 14.2426 | 2000 | #REF! | #REF!
2CP1600 | 1854 | 1173 | 853 | 671 | 653.1523 | 413.2404 | 300.5064 | 236.389 | 35.5968 | 22.5216 | 16.3776 | 12.8832 | 1600 | #REF! | #REF!
2CP3000 | 3066.7 | 1908.9 | 1392.8 | 1106.6 | 1080.3787 | 672.4932 | 490.6745 | 389.8481 | 58.8806 | 36.6509 | 26.7418 | 21.2467 | 3000 | #REF! | #REF!
2CP1200 | 1349 | 865 | 631 | 502 | 475.244 | 304.7339 | 222.2972 | 176.8514 | 25.9008 | 16.608 | 12.1152 | 9.6384 | 1200 | #REF! | #REF!
2CP650 | 776 | 472 | 345 | 274 | 273.3798 | 166.2826 | 121.5413 | 96.5284 | 14.8992 | 9.0624 | 6.624 | 5.2608 | 652 | #REF! | #REF!
VH57 | 1899 | 1200 | 893 | 720 | 669.0055 | 422.7523 | 314.5982 | 253.6514 | 36.4608 | 23.04 | 17.1456 | 13.824 | 1680 | #REF! | #REF!
EN480-2 | 591 | 355 | 254 | 203 | 208.2055 | 125.0642 | 89.4826 | 71.5156 | 11.3472 | 6.816 | 4.8768 | 3.8976 | 489 | #REF! | #REF!
EN160-6 | 197 | 118 | 84.8 | 67.5 | 69.4018 | 41.5706 | 29.8745 | 23.7798 | 3.7824 | 2.2656 | 1.6282 | 1.296 | 163 | #REF! | #REF!
EN320-2 | 394 | 237 | 170 | 135 | 138.8037 | 83.4936 | 59.8899 | 47.5596 | 7.5648 | 4.5504 | 3.264 | 2.592 | 260 | #REF! | #REF!

## Sheet2
SYS A | 1200
SYS B | 1500
SYS A&B | 2700

## Multiroom cooling
Site | AHU | Number of | Room Total | Total | Agreed 75%
TGY | 7.4 | 4 | 29.6 | 121.8 | 91.35
TGY | 13.4 | 3 | 40.2
TGYN02 | 7.4 | 2 | 14.8
TGYN03 | 7.5 | 2 | 15
TGYN04 | 7.4 | 3 | 22.2
CYNTN2 | 18 | 2 | 36 | 96 | 72
CYNTN2 EXT | 30 | 2 | 60
AZTCD1 | 35 | 1 | 35 | 155 | 116.25
AZTCD1 | 30 | 1 | 30
AZTCD2 | 10 | 9 | 90
LCT | 40 | 2 | 80 | 110 | 82.5
LCT EXT | 30 | 1 | 30
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: just showing non redundant numbers (so one extra unit for each line)
Note on A9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2 x 35 + 1 x 30 (so 1 x 35 redundant)