## Plant loading
Key |  |  |  | Not reporting | <70 | 70-80% | 80 - 90 % | >90% | Highlight's cells with non-standard formula
MTX | Power Element Name | Power Element Type | Element Load (A) Jan 24 | Element Load (A) 25/02/24 | Running % load | Total Running Site Load (kW)/(%) | Number of Modules | Module Capacity (kW) | Power Element Capability (kW) | Number of Redundant Modules | Available Capability (kW) | Available Capability (A) | Reserved (A) | Running Load + Reserved (%) | Total Reserved (kW)/(%) | Forecast (A) | Total Forecast (kW)/(%) | Running Load + Reserved+ Forecast (A) | Running Load + Reserved+ Forecast (kW)/(%) | Remaining Element Capability (A) | Remaining Element Capability (kW)/(%) | Total Power Element RAG (% used) | Deployed Usable Capability (% used) | RAG value (for graphing) | Max Technology Load RAG (% used) | Following Power Expansion | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Reserved (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A) | Element Reference (S&P Ref/element name/planned deployment date/requestor) (AC =AC load on DC plant) | Forecast (A)
Text below in RED is for cabs that have been installed but are not yet powered up. BLUE for cabs powered up, not yet fully loaded
Acton | PEAAN | eSure | 622.998 | 629 | 54.46% | 173.528 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 54 | 59.13% | 13.8975 | 5 | 1.526 | 688 | 188.9515 | 467 | 125.786 | 59.57% | 59.98% | 0.59567 | 59.98% |  | 15033/Cage/Feb16/AM | 54 | 23013/Beacon CSTN/AP | 5 | [28 empty] | RAG Status
Acton | PEBAN | eSure | 617.154 | 621 | 53.77% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 54 | 58.44% |  | 9 |  | 684 |  | 471 |  | 59.22% |  | 0.59221 |  |  | 15033/Cage/Feb16/AM | 54 | 23029/BAU ISNG Probes/AP | 9 | [28 empty] | Plant % Used | Site % Remaining
Acton | PECAN | eSure | 472.794 | 462 | 40% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 48 | 44.16% |  | 5 |  | 515 |  | 640 |  | 44.59% |  | 0.44589 |  |  | 15033/Cage/Feb16/AM | 48 | 23013/Beacon CSTN/AP | 5 | [28 empty] | <=70
Acton | PEFAN | eSure | 701.839 | 713 | 61.73% | 55.09% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 50 | 66.06% | 4.412% | 0 | 0.4844% | 763 | 59.98% | 392 | 39.93% | 66.06% |  | 0.66061 |  |  | 15033/Cage/Feb16/AM | 50 | [30 empty] | 70-80
Acton | PEGAN | eSure | 750.271 | 759 | 65.71% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 49 | 69.96% |  | 9 |  | 817 |  | 338 |  | 70.74% |  | 0.70736 |  |  | 15033/Cage/Feb16/AM | 49 | 23029/BAU ISNG Probes/AP | 9 | [28 empty] | 80-90
Basingstoke | PEABE | eSure | 850.285 | 816 | 70.65% | 372.671 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 83 | 77.84% | 39.022 | 73.5 | 57.6065 | 972.5 | 469.2995 | 182.5 | 34.2805 | 84.2% | 93.11% | 0.84199 | 93.11% |  | Total res'd for NFV | 83 | 23026/Fortinet/AP | 10 | 23018/Security TSR/AP | 36 | 23029/BAU ISNG Probes/AP | 27.5 | [24 empty] | >90
Basingstoke | PEBBE | eSure | 829.374 | 840 | 72.73% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 70 | 78.79% |  | 174 |  | 1084 |  | 71 |  | 93.85% |  | 0.93853 |  |  | Total res'd for NFV | 70 |  |  | 23018/NFV TSR/AP | 174
Basingstoke | PECBE | eSure | 920.886 | 809 | 70.04% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 44 | 73.85% |  | 136 |  | 989 |  | 166 |  | 85.63% |  | 0.85628 |  |  | Total res'd for NFV | 44 | 22009/M-CE Increases/AP |  | 23018/NFV TSR/AP | 126 | 23026/Fortinet/AP | 10
Basingstoke | PEEBE | eSure | 880.438 | 869 | 75.24% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 81 | 82.25% |  | 122.5 |  | 1072.5 |  | 82.5 |  | 92.86% |  | 0.92857 |  |  | Total res'd for NFV | 81 | 23007/M-PE 9912/AP | 95 | 23029/BAU ISNG Probes/AP | 27.5
Basingstoke | PEFBE | eSure | 853.706 | 847 | 73.33% | 73.94% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 90 | 81.13% | 7.742% | 235 | 11.43% | 1172 | 93.11% | -17 | 6.802% | 101.5% |  | 1.0147 |  |  | Total res'd for NFV | 90 | 23007/M-PE 9912/AP | 95 | 23018/NFV TSR/AP | 104 | 23018/Security TSR/AP | 36
Basingstoke | PEGBE | eSure | 864.712 | 878 | 76.02% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 120 | 86.41% |  | 103 |  | 1101 |  | 54 |  | 95.32% |  |  |  |  | Total res'd for NFV | 120 |  |  | 23018/NFV TSR/AP | 103
Basingstoke | PEHBE | eSure | 863.348 | 872 | 75.5% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 127 | 86.49% |  | 87 |  | 1086 |  | 69 |  | 94.03% |  | 0.94026 |  |  | Total res'd for NFV | 127 |  |  | 23018/NFV TSR/AP | 87
Basingstoke | PEIBE | eSure | 889.778 | 907 | 78.53% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 101 | 87.27% |  | 126 |  | 1134 |  | 21 |  | 98.18% |  | 0.98182 |  |  | Total res'd for NFV | 101 |  |  | 23018/NFV TSR/AP | 126
Crawley | PEACY | eSure | 388.804 | 391 | 33.85% | 126.44 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 33.85% | 0 | 15 | 8.066 | 406 | 134.506 | 749 | 180.2315 | 35.15% | 42.7% | 0.35152 | 42.7% |  |  |  | 24001/SPARC T8-2/LP (AC) | 15
Crawley | PEBCY | eSure | 496.376 | 497 | 43.03% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 43.03% |  | 15 |  | 512 |  | 643 |  | 44.33% |  | 0.44329 |  |  |  |  | 24001/SPARC T8-2/LP (AC) | 15
Crawley | PECCY | eSure | 604.883 | 609 | 52.73% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 52.73% |  | 15 |  | 624 |  | 531 |  | 54.03% |  | 0.54026 |  |  |  |  | 24001/SPARC T8-2/LP (AC) | 15
Crawley | PEDCY | eSure | 469.417 | 472 | 40.87% | 40.14% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 40.87% | 0% | 59 | 2.561% | 531 | 42.7% | 624 | 57.22% | 45.97% |  | 0.45974 |  |  |  |  | 20029/RedstreamEvo/AP(SP) | 44 | 24001/SPARC T8-2/LP (AC) | 15
Crawley | PEECY | eSure | 349.363 | 351 | 30.39% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 30.39% |  | 44 |  | 395 |  | 760 |  | 34.2% |  | 0.34199 |  |  |  |  | 20029/RedstreamEvo/AP(SP) | 44
Edinburgh | PECEH | eSure | 845.371 | 836 | 72.38% | 285.6345 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 193 | 89.09% | 65.1275 | 39.5 | 6.3765 | 1068.5 | 357.1385 | 86.5 | 20.5465 | 92.51% | 94.48% | 0.92511 | 94.48% | #DIV/0! | NFV reserved loads updated 11/10/23 | 193 | 23014/Beacon CSTN/AP | 15 | 23028/IPAR/AP (AC) | 4.5 | 23027/ISNG Probes/LP | 20
Edinburgh | PEDEH | eSure | 913.211 | 899 | 77.84% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 189 | 94.2% |  | 4.5 |  | 1092.5 |  | 62.5 |  | 94.59% |  | 0.94589 |  |  | Total res'd for NFV | 189 |  |  | 23028/IPAR/AP (AC) | 4.5
Edinburgh | PEEEH | eSure | 869.746 | 865 | 74.89% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 185 | 90.91% |  | 24.5 |  | 1074.5 |  | 80.5 |  | 93.03% |  | 0.9303 |  |  | Total res'd for NFV | 185 |  |  | 23028/IPAR/AP (AC) | 4.5 | 23027/ISNG Probes/LP | 20
Edinburgh | PEFEH | eSure | 834.984 | 824 | 71.34% | 75.56% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 163 | 85.45% | 17.23% | 39.5 | 1.687% | 1026.5 | 94.48% | 128.5 | 5.436% | 88.87% |  | 0.88874 |  |  | Total res'd for NFV | 163 | 23014/Beacon CSTN/AP | 15 | 23028/IPAR/AP (AC) | 4.5 | 23027/ISNG Probes/LP | 20
Edinburgh | PEGEH | eSure | 925.312 | 944 | 81.73% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 189 | 98.1% |  | 4.5 |  | 1137.5 |  | 17.5 |  | 98.48% |  |  |  |  | Total res'd for NFV | 189 |  |  | 23028/IPAR/AP (AC) | 4.5
Edinburgh | PEHEH | eSure | 877.235 | 873 | 75.58% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 276 | 99.48% |  | 4.5 |  | 1153.5 |  | 1.5 |  | 99.87% |  |  |  |  | Total res'd for NFV | 276 |  |  | 23028/IPAR/AP (AC) | 4.5
Esher | PEDER | eSure | 412.656 | 415 | 35.93% | 83.0035 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 35.93% | 0 | 0 | 0 | 415 | 83.0035 | 740 | 168.7865 | 35.93% | 32.94% | 0.35931 | 27.67%
Esher | PEEER | eSure | 369.976 | 371 | 32.12% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 32.12% |  | 0 |  | 371 |  | 784 |  | 32.12% |  | 0.32121
Esher | PEFER | eSure | 436.082 | 426 | 36.88% | 32.94% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 36.88% | 0% | 0 | 0% | 426 | 32.94% | 729 | 66.98% | 36.88% |  | 0.36883
Esher | PEGER | eSure | 308.471 | 311 | 26.93% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 26.93% |  | 0 |  | 311 |  | 844 |  | 26.93% |  | 0.26926
Gloucester | PEAGR | eSure | 637.257 | 641 | 55.5% | 260.183 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 178 | 70.91% | 119.8455 | 16.7 | 31.5664 | 835.7 | 411.5949 | 319.3 | 53.1266 | 72.35% | 88.52% | 0.72355 | 88.52% | #DIV/0! | Total res'd for NFV | 178 |  |  | 23025/Hawk/AP (AC) | 10.3 | 22024/NFV DELL Store/AP (AC) | 6.4
Gloucester | PEBGR | eSure | 763.176 | 765 | 66.23% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 178 | 81.65% |  | 16.7 |  | 959.7 |  | 195.3 |  | 83.09% |  | 0.83091 |  |  | Total res'd for NFV | 178 |  |  | 23025/Hawk/AP (AC) | 10.3 | 22024/NFV DELL Store/AP (AC) | 6.4
Gloucester | PECGR | eSure | 715.404 | 716 | 61.99% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 237 | 82.51% |  | 511.7 |  | 1464.7 |  | -309.7 |  | 126.8% |  | 1.2681 |  |  | Total res'd for NFV | 237 | 23024/ Additional 11 RMS/AP | 495 | 23025/Hawk/AP (AC) | 10.3 | 22024/NFV DELL Store/AP (AC) | 6.4
Gloucester | PEDGR | eSure | 713.649 | 711 | 61.56% | 55.95% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 247 | 82.94% | 25.77% | 16.7 | 6.788% | 974.7 | 88.52% | 180.3 | 11.43% | 84.39% |  | 0.8439 |  |  | Total res'd for NFV | 247 | 23024/ Additional 11 RMS/AP |  | 23025/Hawk/AP (AC) | 10.3 | 22024/NFV DELL Store/AP (AC) | 6.4
Gloucester | PEEGR | eSure | 714.006 | 705 | 61.04% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 219 | 80% |  | 0 |  | 924 |  | 231 |  | 80% |  | 0.8 |  |  | Total res'd for NFV | 219
Gloucester | GCRMTX-DCSYS06a | NPR48-ES | 639 | 639 | 46.44% |  | 51 | 3 | 153 | 26 | 75 | 1376 | 547 | 86.19% |  | 8.7 |  | 1194.7 |  | 181.3 |  | 86.82% |  |  |  |  | Total res'd for NFV | 547 | 23011/Compute 421/AP | 6.5 | 230xx/HPE Store/AP | 2.2
Gloucester | GCRMTX-DCSYS06b | NPR48-ES | 597 | 597 | 43.39% |  | 51 | 3 | 153 | 26 | 75 | 1376 | 593 | 86.48% |  | 8.7 |  | 1198.7 |  | 177.3 |  | 87.11% |  |  |  |  | Total res'd for NFV | 593 | 23011/Compute 421/AP | 6.5 | 230xx/HPE Store/AP | 2.2
Gravelly Hill | BMGMTX-DCSYS01 | HDR48-ES | 757 | 766 | 66.32% | 295.172 | 44 | 3 | 132 | 23 | 63 | 1155 | 20 | 68.05% | 67.3075 | 54 | 20.3884 | 840 | 382.8679 | 315 | 78.747 | 72.73% | 82.87% | 0.72727 | 82.87% | #REF! | Total res'd for NFV | 20 | 20049/RSE/AP(SP) | 20 | 23022/A2/AP | 24 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | BMGMTX-DCSYS02 | HDR48-ES | 785 | 785 | 67.97% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 56 | 72.81% |  | 47 |  | 888 |  | 267 |  | 76.88% |  | 0.76883 |  |  | Total res'd for NFV | 56 | 20049/RSE/AP(SP) | 19 | 23029/BAU ISNG Probes/AP | 18 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | PECGL | eSure | 784 | 858 | 74.29% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 151 | 87.36% |  | 28 |  | 1037 |  | 118 |  | 89.78% |  | 0.89784 |  |  | Total res'd for NFV | 151 |  |  | 23029/BAU ISNG Probes/AP | 18 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | BMGMTX-DCSYS04 | HDR48-ES | 810 | 797 | 69% | 63.89% | 44 | 3 | 132 | 23 | 63 | 1155 | 159 | 82.77% | 14.57% | 10 | 4.413% | 966 | 82.87% | 189 | 17.04% | 83.64% |  | 0.83636 |  |  | Total res'd for NFV | 159 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | BMGMTX-DCSYS05 | HDR48-ES | 797 | 799 | 69.18% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 104 | 78.18% |  | 10 |  | 913 |  | 242 |  | 79.05% |  | 0.79048 |  |  | Total res'd for NFV | 104 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | PEFGL | eSure | 828 | 844 | 73.07% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 187 | 89.26% |  | 10 |  | 1041 |  | 114 |  | 90.13% |  | 0.9013 |  |  | Total res'd for NFV | 187 | 24003/AC Util 03/LP (AC) | 10
Gravelly Hill | BMGMTX-DCSYS07a | NPR48-ES | 284 | 284 | 36.88% |  | 29 | 3 | 87 | 15 | 42 | 770 | 279 | 73.12% |  | 107.4 |  | 670.4 |  | 99.6 |  | 87.06% |  | 0.87065 |  |  | Total res'd for NFV | 279 | 22013/M-PE 9912/AP | 95.1 | 22022/M-PE Wavserver Ai/AP | 12.3
Gravelly Hill | BMGMTX-DCSYS07b | NPR48-ES | 283 | 283 | 36.75% |  | 29 | 3 | 87 | 15 | 42 | 770 | 279 | 72.99% |  | 107.7 |  | 669.7 |  | 100.3 |  | 86.97% |  | 0.86974 |  |  | Total res'd for NFV | 279 | 22013/M-PE 9912/AP | 95.1 | 22022/M-PE Wavserver Ai/AP | 12.6
Kings Cross | PEAKS | eSure | 257.309 | 248 | 32.21% | 127.4755 | 24 | 3.5 | 84 | 12 | 42 | 770 | 0 | 32.21% | 0 | 0 | 0 | 248 | 127.4755 | 522 | 270.2655 | 32.21% | 32.03% | 0.32208 | 26.39%
Kings Cross | PEBKS | eSure | 358.273 | 352 | 36.9% |  | 30 | 3.5 | 105 | 15 | 52 | 954 | 0 | 36.9% |  | 0 |  | 352 |  | 602 |  | 36.9% |  | 0.36897
Kings Cross | PEEKS | eSure | 101.516 | 100 | 25.97% |  | 12 | 3.5 | 42 | 6 | 21 | 385 | 0 | 25.97% |  | 0 |  | 100 |  | 285 |  | 25.97% |  | 0.25974
Kings Cross | PEIKS | eSure | 531.315 | 528 | 45.71% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 45.71% |  | 0 |  | 528 |  | 627 |  | 45.71% |  | 0.45714
Kings Cross | PEJKS | eSure | 315 | 229 | 19.83% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 19.83% |  | 0 |  | 229 |  | 926 |  | 19.83% |  | 0.19827
Kings Cross | PEKKS | eSure | 526.933 | 484 | 50.73% | 32.03% | 30 | 3.5 | 105 | 15 | 52 | 954 | 0 | 50.73% | 0% | 0 | 0% | 484 | 32.03% | 470 | 67.91% | 50.73% |  | 0.50734
Kings Cross | PELKS | eSure | 162.224 | 161 | 20.91% |  | 24 | 3.5 | 84 | 12 | 42 | 770 | 0 | 20.91% |  | 0 |  | 161 |  | 609 |  | 20.91% |  | 0.20909
Kings Cross | PEMKS | eSure | 146.784 | 146 | 18.96% |  | 24 | 3.5 | 84 | 12 | 42 | 770 | 0 | 18.96% |  | 0 |  | 146 |  | 624 |  | 18.96% |  | 0.18961
Kings Cross | PENKS | eSure | 100.584 | 91 | 23.64% |  | 12 | 3.5 | 42 | 6 | 21 | 385 | 0 | 23.64% |  | 0 |  | 91 |  | 294 |  | 23.64% |  | 0.23636
Leyland | LLDMTX-DCSYS01 | HDR48-ES | 907 | 901 | 78.01% | 331.251 | 44 | 3 | 132 | 23 | 63 | 1155 | 66 | 83.72% | 55.917 | 51 | 7.085 | 1018 | 394.253 | 137 | 72.1595 | 88.14% | 85.71% | 0.88139 | 85.71% | #REF! | Total res'd for NFV | 66 | 23016/NFV CV 101/AP (AC) | 7 | 24002/RLS-Ciena cab3/GD | 17 | 23029/BAU ISNG Probes/AP | 18 | 24000/ISNG Probe/LP | 9
Leyland | LLDMTX-DCSYS02 | HDR48-ES | 805 | 810 | 70.13% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 98 | 78.61% |  | 42 |  | 950 |  | 205 |  | 82.25% |  | 0.82251 |  |  | Total res'd for NFV | 98 | 23016/NFV CV 101/AP (AC) | 7 | 24002/RLS-Ciena cab3/GD | 17 | 23029/BAU ISNG Probes/AP | 18
Leyland | LLDMTX-DCSYS03 | HDR48-ES | 934 | 929 | 80.43% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 85 | 87.79% |  | 16 |  | 1030 |  | 125 |  | 89.18% |  | 0.89177 |  |  | Total res'd for NFV | 85 | 23016/NFV CV 101/AP (AC) | 7 |  |  | 24000/ISNG Probe/LP | 9
Leyland | LLDMTX-DCSYS04 | HDR48-ES | 860 | 859 | 74.37% | 72.01% | 44 | 3 | 132 | 23 | 63 | 1155 | 66 | 80.09% | 12.16% | 7 | 1.54% | 932 | 85.71% | 223 | 15.69% | 80.69% |  | 0.80693 |  |  | Total res'd for NFV | 66 | 23016/NFV CV 101/AP (AC) | 7
Leyland | LLDMTX-DCSYS05 | HDR48-ES | 909 | 910 | 78.79% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 79 | 85.63% |  | 7 |  | 996 |  | 159 |  | 86.23% |  | 0.86234 |  |  | Total res'd for NFV | 79 | 23016/NFV CV 101/AP (AC) | 7
Leyland | LLDMTX-DCSYS06 | HDR48-ES | 900 | 898 | 77.75% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 69 | 83.72% |  | 7 |  | 974 |  | 181 |  | 84.33% |  | 0.84329 |  |  | Total res'd for NFV | 69 | 23016/NFV CV 101/AP (AC) | 7
Leyland | LLDMTX-DCSYS07a | NPR48-ES | 386 | 385 | 41.18% |  | 35 | 3 | 105 | 18 | 51 | 935 | 282 | 71.34% |  | 0 |  | 667 |  | 249 |  | 71.34% |  | 0.71337 |  |  | Total res'd for NFV | 282
Leyland | LLDMTX-DCSYS07b | NPR48-ES | 382 | 386 | 41.28% |  | 35 | 3 | 105 | 18 | 51 | 935 | 281 | 71.34% |  | 0 |  | 667 |  | 412 |  | 71.34% |  | 0.71337 |  |  | Total res'd for NFV | 281
Milton Keynes | PEAMS | eSure | 1047.611 | 1046 | 78.12% | 367.766 | 42 | 3.5 | 147 | 21 | 73 | 1339 | 59 | 82.52% | 28.7215 | 182.5 | 46.107 | 1287.5 | 442.5945 | 51.5 | 37.2235 | 96.15% | 92.21% | 0.96154 | 92.02% | #DIV/0! | Total res'd for NFV | 59 | 23018/NFV TSR/AP | 97 | 23022/A2/AP | 12 | 23026/Fortinet/AP | 10 | 23018/Security TSR/AP | 36 | 23029/BAU ISNG Probes/AP | 27.5
Milton Keynes | PEBMS | eSure | 989.083 | 988 | 73.79% |  | 42 | 3.5 | 147 | 21 | 73 | 1339 | 67 | 78.79% |  | 170 |  | 1225 |  | 114 |  | 91.49% |  | 0.91486 |  |  | Total res'd for NFV | 67 | 23018/NFV TSR/AP | 158 | 23022/A2/AP | 12
Milton Keynes | PECMS | eSure | 960.893 | 960 | 71.7% |  | 42 | 3.5 | 147 | 21 | 73 | 1339 | 85 | 78.04% |  | 211.5 |  | 1256.5 |  | 82.5 |  | 93.84% |  | 0.93839 |  |  | Total res'd for NFV | 85 | 23018/NFV TSR/AP | 184 | 23029/BAU ISNG Probes/AP | 27.5
Milton Keynes | PEDMS | eSure | 1132.436 | 1131 | 84.47% | 76.62% | 42 | 3.5 | 147 | 21 | 73 | 1339 | 91 | 91.26% | 5.984% | 80 | 9.606% | 1302 | 92.21% | 37 | 7.755% | 97.24% |  | 0.97237 |  |  | Total res'd for NFV | 91 | 23018/NFV TSR/AP | 34 | 23026/Fortinet/AP | 10 | 23018/Security TSR/AP | 36
Milton Keynes | PEEMS | eSure | 1058.541 | 1051 | 78.49% |  | 42 | 3.5 | 147 | 21 | 73 | 1339 | 46 | 81.93% |  | 69 |  | 1166 |  | 173 |  | 87.08% |  | 0.8708 |  |  | Total res'd for NFV | 46 | 23018/NFV TSR/AP | 69
Milton Keynes | PEFMS | eSure | 1041.864 | 1045 | 78.04% |  | 42 | 3.5 | 147 | 21 | 73 | 1339 | 59 | 82.45% |  | 87 |  | 1191 |  | 148 |  | 88.95% |  | 0.88947 |  |  | Total res'd for NFV | 59 | 23018/NFV TSR/AP | 87
Milton Keynes | MKSMTX-DCSYS07a | NPR48-ES | 261 | 261 | 67.79% |  | 16 | 3 | 48 | 9 | 21 | 385 | 60 | 83.38% |  | 23 |  | 344 |  | 41 |  | 89.35% |  | 0.89351 |  |  | Total res'd for NFV | 60 | 23018/NFV TSR/AP | 23
Milton Keynes | MKSMTX-DCSYS07b | NPR48-ES | 266 | 266 | 69.09% |  | 16 | 3 | 48 | 9 | 21 | 385 | 60 | 84.68% |  | 23 |  | 349 |  | 36 |  | 90.65% |  | 0.90649 |  |  | Total res'd for NFV | 60 | 23018/NFV TSR/AP | 23
Oldham | OLDMTX-DCSYS01 | HDR48-ES | 891 | 887 | 76.8% | 293.21 | 44 | 3 | 132 | 23 | 63 | 1155 | 161 | 90.74% | 105.5665 | 0 | 16.241 | 1048 | 415.0175 | 107 | 49.595 | 90.74% | 89.25% | 0.90736 | 88.68% | #DIV/0! | Total res'd for NFV | 161
Oldham | OLDMTX-DCSYS02 | HDR48-ES | 820 | 818 | 70.82% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 214 | 89.35% |  | 9 |  | 1041 |  | 114 |  | 90.13% |  | 0.9013 |  |  | Total res'd for NFV | 214 |  |  | 23029/BAU ISNG Probes/AP | 9
Oldham | OLDMTX-DCSYS03 | HDR48-ES | 822 | 820 | 71% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 103 | 79.91% |  | 101 |  | 1024 |  | 131 |  | 88.66% |  | 0.88658 |  |  | Total res'd for NFV | 103 | 22013/M-PE 9912/AP | 92 | 23029/BAU ISNG Probes/AP | 9
Oldham | OLDMTX-DCSYS04 | HDR48-ES | 621 | 615 | 69.89% | 63.06% | 34 | 3 | 102 | 18 | 48 | 880 | 198 | 92.39% | 22.7% | 0 | 3.493% | 813 | 89.25% | 67 | 10.67% | 92.39% |  | 0.92386 |  |  | Total res'd for NFV | 198
Oldham | OLDMTX-DCSYS05 | HDR48-ES | 636 | 637 | 55.15% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 158 | 68.83% |  | 140 |  | 935 |  | 220 |  | 80.95% |  | 0.80952 |  |  | Total res'd for NFV | 158 | 22013/M-PE 9912/AP | 92 | 20042&22022/OptExpress x3 cabs/Nov20/AP(SP) | 48
Oldham | OLDMTX-DCSYS06 | HDR48-ES | 646 | 652 | 56.45% |  | 44 | 3 | 132 | 23 | 63 | 1155 | 228 | 76.19% |  | 48 |  | 928 |  | 227 |  | 80.35% |  | 0.80346 |  |  | Total res'd for NFV | 228 | 20042&22022/OptExpress x3 cabs/Nov20/AP(SP) | 48
Oldham | OLDMTX-DCSYS07a | NPR48-ES | 470 | 480 | 51.34% |  | 36 | 3 | 108 | 19 | 51 | 935 | 418 | 96.04% |  | 0 |  | 898 |  | 37 |  | 96.04% |  | 0.96043 |  |  | Total res'd for NFV | 418
Oldham | OLDMTX-DCSYS07b | NPR48-ES | 462 | 471 | 50.37% |  | 36 | 3 | 108 | 19 | 51 | 935 | 457 | 99.25% |  | 0 |  | 928 |  | 7 |  | 99.25% |  | 0.99251 |  |  | Total res'd for NFV | 457
Rotherham | PEARM | eSure | 400.468 | 401 | 34.72% | 100.2255 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 34.72% | 0 | 0 | 14.715 | 401 | 114.9405 | 754 | 199.797 | 34.72% | 36.49% | 0.34719 | 36.49%
Rotherham | PEBRM | eSure | 437.985 | 437 | 37.84% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 37.84% |  | 65 |  | 502 |  | 653 |  | 43.46% |  | 0.43463 | [6 empty] | 22019/Huawei BSC/AP | 65
Rotherham | PECRM | eSure | 532.697 | 533 | 46.15% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 46.15% |  | 65 |  | 598 |  | 557 |  | 51.77% |  | 0.51775 |  |  |  |  | 22019/Huawei BSC/AP | 65
Rotherham | PEDRM | eSure | 255.944 | 256 | 22.16% | 31.82% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 22.16% | 0% | 70 | 4.671% | 326 | 36.49% | 829 | 63.43% | 28.23% |  | 0.28225 |  |  |  |  | 20011/OpenRAN/Apr20/AP | 70
Rotherham | PEERM | eSure | 211.459 | 212 | 18.35% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 18.35% |  | 70 |  | 282 |  | 873 |  | 24.42% |  | 0.24416 |  |  |  |  | 20011/OpenRAN/Apr20/AP | 70
Southampton | PEASN | eSure | 385 | 368 | 31.86% | 95.3205 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 31.86% | 0 | 0 | 18.748 | 368 | 114.0685 | 787 | 137.7215 | 31.86% | 45.27% | 0.31861 | 38.02%
Southampton | PEBSN | eSure | 562 | 544 | 47.1% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 47.1% |  | 172 |  | 716 |  | 439 |  | 61.99% |  | 0.61991 |  |  |  |  | 20035/AMITIE/Sept20/AP(RL) | 107 | 22019/Huawei BSC BHISN/AP | 65
Southampton | PECSN | eSure | 497 | 491 | 42.51% | 37.83% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 42.51% | 0% | 172 | 7.44% | 663 | 45.27% | 492 | 54.65% | 57.4% |  | 0.57403 |  |  |  |  | 20035/AMITIE/Sept20/AP(RL) | 107 | 22019/Huawei BSC BHISN /AP | 65
Southampton | PEESN | eSure | 353 | 346 | 29.96% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 29.96% |  | 0 |  | 346 |  | 809 |  | 29.96% |  | 0.29957
Swanley | PEASY | eSure | 544.639 | 538 | 46.58% | 111.7795 | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 46.58% | 0 | 0 | 0 | 538 | 111.7795 | 617 | 192.0035 | 46.58% | 36.77% | 0.4658 | 36.71%
Swanley | PEBSY | eSure | 469.683 | 498 | 43.12% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 43.12% |  | 0 |  | 498 |  | 657 |  | 43.12% |  | 0.43117
Swanley | PECSY | eSure | 384.775 | 384 | 33.25% |  | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 33.25% |  | 0 |  | 384 |  | 771 |  | 33.25% |  | 0.33247
Swanley | PEDSY | eSure | 296.403 | 298 | 25.8% | 36.77% | 36 | 3.5 | 126 | 18 | 63 | 1155 | 0 | 25.8% | 0% | 0 | 0% | 298 | 36.77% | 857 | 63.16% | 25.8% |  | 0.25801
Swanley | PEESY | eSure | 311.686 | 333 | 34.91% |  | 30 | 3.5 | 105 | 15 | 52 | 954 | 0 | 34.91% |  | 0 |  | 333 |  | 621 |  | 34.91% |  | 0.34906
Bristol | PEFBL | NetSure | 473.663 | 476 | 45.55% | 43.8725 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 41 | 5.0685 | 517 |  | 528 | 64.964 | 49.47% | [6 empty] | 22019/Huawei BSC/AP | 41
Bristol | PEHBL | NetSure | 330.273 | 329 | 31.48% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 52 |  | 381 |  | 664 |  | 36.46% | [6 empty] | 22019/Huawei BSC/AP | 52
Cardiff | PECCF | NetSure | 348.906 | 352 | 33.68% | 39.6215 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 44 | 4.796 | 396 |  | 649 | 68.452 | 37.89% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44
Cardiff | PEDCF | NetSure | 165.07 | 165 | 32.16% |  | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  |  | 44 |  | 209 |  | 304 |  | 40.74% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44
Cardiff | PEECF | NetSure | 209.479 | 210 | 40.94% |  | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  |  | 0 |  | 210 |  | 303 |  | 40.94%
Carlisle | PEACE | NetSure | 400 | 400 | 38.28% | 45.998 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 134 | 14.606 | 534 |  | 511 |  | 51.1% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44 | 20041/OptExpress x3 cabs/Nov20/AP(SP) | 48 | 22008/M-PE/M-CE Upgrade/AP | 13 | 22016/E/// BSC/Sep22/AP | 29
Carlisle | PEBCE | NetSure | 439 | 444 | 42.49% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 134 |  | 578 |  | 467 |  | 55.31% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44 | 20041/OptExpress x3 cabs/Nov20/AP(SP) | 48 | 22008/M-PE/M-CE Upgrade/AP | 13 | 22016/E/// BSC/Sep22/AP | 29
Croydon | PEFCN | NetSure | 313 | 313 | 29.95% | 38.15 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 44 | 4.796 | 357 |  | 688 |  | 34.16% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44
Croydon | PEGCN | NetSure | 389 | 387 | 37.03% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 44 |  | 431 |  | 614 |  | 41.24% | [6 empty] | 20029/RedstreamEvo/AP(SP) | 44
Glasgow TXO | PEJGW | eSure | 86 | 87 | 22.6% | 9.374 | 9 | 3.5 | 31 | 3 | 21 | 385 | 0 |  | 0 | 0 | 0 | 87 |  | 298 |  | 22.6%
Glasgow TXO | PEKGW | eSure | 84 | 85 | 22.08% |  | 9 | 3.5 | 31 | 3 | 21 | 385 | 0 |  |  | 0 |  | 85 |  | 300 |  | 22.08%
Leicester | PEFLR | NetSure | 626 | 626 | 59.9% | 62.457 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 0 | 0 | 626 |  | 419 |  | 59.9%
Leicester | PEGLR | NetSure | 519 | 520 | 49.76% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 0 |  | 520 |  | 525 |  | 49.76%
Newbury | PEGNY | NetSure | 366 | 366 | 35.02% | 37.06 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 0 | 0 | 366 |  | 679 |  | 35.02%
Newbury | PEHNY | NetSure | 312 | 314 | 30.05% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 0 |  | 314 |  | 731 |  | 30.05%
Newcastle | PEENE | NetSure | 306 | 306 | 29.28% | 44.472 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 59 | 8.611 | 365 |  | 680 |  | 34.93% | [6 empty] | 22016/E/// x2 BSC/Sep22/AP | 59
Newcastle | PEFNE | NetSure | 361 | 359 | 34.35% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 79 |  | 438 |  | 607 |  | 41.91% | [6 empty] | 22008/M-PE/M-CE Upgrade/AP | 20 | 22016/E/// x2 BSC/Sep22/AP | 59
Newcastle | PEGNE | NetSure | 147 | 151 | 29.43% |  | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  |  | 20 |  | 171 |  | 342 |  | 33.33% | [6 empty] | 22008/M-PE/M-CE Upgrade/AP | 20
Oxford | PECOD | NetSure | 236 | 236 | 22.58% | 20.383 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 107 | 11.663 | 343 |  | 702 |  | 32.82% | [6 empty] | 20035/AMITIE/Sept20/AP | 107
Oxford | PEFOD | NetSure | 138 | 138 | 15.68% |  | 30 | 3.2 | 96 | 15 | 48 | 880 | 0 |  |  | 107 |  | 245 |  | 635 |  | 27.84% | [6 empty] | 20035/AMITIE/Sept20/AP | 107
Stafford | PEESD | NetSure | 380 | 394 | 37.7% | 44.1995 | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  | 0 | 0 | 0 | 394 |  | 651 |  | 37.7%
Stafford | PEGSD | NetSure | 447 | 417 | 39.9% |  | 36 | 3.2 | 115 | 18 | 57 | 1045 | 0 |  |  | 0 |  | 417 |  | 628 |  | 39.9%
Warrington TXO | PELWN | NetSure | 208.912 | 209 | 40.74% | 39.567 | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  | 0 | 0 | 0 | 209 |  | 304 |  | 40.74%
Warrington TXO | PEMWN | NetSure | 156.163 | 156 | 30.41% |  | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  |  | 0 |  | 156 |  | 357 |  | 30.41%
Warrington TXO | PENWN | NetSure | 360.743 | 361 | 70.37% |  | 18 | 3.2 | 57 | 9 | 28 | 513 | 0 |  |  | 0 |  | 361 |  | 152 |  | 70.37%
| Total VF-UK Network | [5 empty] | VF-UK Type A Sites
| Number of Elements | Module Count |  | Total Capacity |  |  | Number of Plants | Rectifier Count | Total Capacity
|  |  | (kW) | (kW) |  | (MW) |  |  | (kW) | (MW)
NetSure | 23 | 714 | 0 | 2278 |  | 2.278 | 0 | 0 | 0 | 0
eSure | 66 | 2256 | 0 | 7895 |  | 7.895 | 64 | 2238 | 7833 | 7.833
NPR48-ES | 10 | 334
HDR48-ES | 16 | 694
Total DC Capacity (Type A) (MW) | 7.833
Total eSure Capacity (Type A) as % of Total DC | 100%
Total Battery Capaicty (Type A) (Ah) | 265320
Total AC (inverter) Capacity (Type A) (kVA) | 1557.6
Total Bravo Capacity (type A) as % of Total AC | 3.852%
Note on V2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Red text =<20%
Note on AB9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note to comment Based on recorded readings as per forecasting spreadsheet Reply: NFV Loads reviewed 20/04/2022 Reply: NFV reserved loads updated on 26/07/2022 Reply: NFV reserved loads updated on 23/12/2022 Reply: NFV reserved loads updated on 27/02/2023 Reply: NFV reserved loads updated on 25/07/2023 Reply: NFV reserved loads updated on 12/12/23
Note on AB22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on recorded readings as per forecasting spreadsheet Reply: NFV loads reviewed 20/04/2022 Reply: NFV reserved loads updated on 26/07/2022 Reply: NFV reserved loads updated on 3/10/2022 Reply: NFV reserved loads updated on 23/12/2022 Reply: NFV reserved loads updated on 25/07/23 Reply: NFV reserved loads updated on 25/08/2023 Reply: NFV reserved loads updated on 11/10/2023
Note on AC22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20A removed from PECEH reserved load for ISNG probes (23027) as for NFV probing
Note on AC24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20A removed from PEEEH reserved load for ISNG probes (23027) as for NFV probing
Note on AC25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20A removed from PEFEH reserved load for ISNG probes (23027) as for NFV probing
Note on AC27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HGW Due to move onto NFV will reduce the load by 5kW
Note on X32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DCSYS06a & b 28.8kW of the 75kW capacity is reserved for the AC system
Note on Z32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: DCSYS06a & b 28.8kW of the 75kW capacity is reserved for the AC system
Note on AB32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New NFV Live and reserved loads added 14/06/2022 Reply: NFV reserved loads updated on 26/08/2022 Synergy Frames capacity reduced from 7.5kW to 6kW Reply: NFV Live load readings taken 10/10/2022 reserved updated Reply: NFV reserved loads updated on 29/12/2022 Reply: NFV reserved loads reviewed Reply: NFV reserved loads updated 26/09/2023 Reply: NFV reserved loads reviewed 02/11/23 Reply: NFV reserved loads updated on 13th Dec 23 Reply: NFV reserved loads updated on 21st Dec Reply: NFV reserved loads updated on 20th Feb
Note on AD34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: allows S2R to deliver for 3 site 6M SAU delivery Reply: Proposed location 194/195 hence C&D
Note on B37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 28.8kW of the 75kW capacity is reserved for the AC system
Note on D37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load figure is the total load for AC and DC
Note on E37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load figure is the total load for AC and DC
Note on L37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 28.8kW of the 75kW capacity is reserved for the AC system Reply: Useable DC capacity is 59 without reducing AC capacity Reply: Added the 16kW AC capacity into the DC figures. Only 59kW useable Reply: Cells highlighted to show includes Inverter capacity
Note on B38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 28.8kW of the 75kW capacity is reserved for the AC system
Note on D38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load figure is the total load for AC and DC
Note on E38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load figure is the total load for AC and DC
Note on L38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 28.8kW of the 75kW capacity is reserved for the AC system Reply: Useable DC capacity is 59 without reducing AC capacity Reply: Added the 16kW AC capacity into the DC figures. Only 59kW useable Reply: Cells highlighted to show includes Inverter capacity
Note on AB39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NFV reserved loads updated & Synergy frames capacity reduce from 7.5kW to 6kW on 26/08/2022 Reply: NFV Load review undertook on 19th Dec 22 Reply: NFV Load review undertook on 20th Feb-23 Reply: NFV Load review undertaken Reply: NFV loads review undertaken Reply: NFV reserved loads updated 11/12/23
Note on AE39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 45A allocated
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Being migrated to DCSYS02
Note on E40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Being migrated to DCSYS02
Note on AE40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 45A allocated
Note on D41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Possible controller failure 29/11/23, rectified 18/01/24
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last update 11/02/24
Note on H53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 07/01/21 x6 removed for use at XEH
Note on H54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 07/01/21 x6 removed for use at XEH
Note on H55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 07/01/21 x24 removed for use at XEH
Note on V56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 20kW reduction to align with bldg capability (480kW reduced to 460kW)
Note on X56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Max tech load fig used (460kW) as lower than deployed usable capability (480kW)
Note on AB56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on recorded readings as per forecasting spreadsheet Reply: NFV loads reviewed 20/04/2022 Reply: NFV reserved loads updated on 26/7/2022 Reply: NFV Load review undertook on 19th Dec Reply: NFV load review undertaken on 27/02/2023 Reply: NFV Load review undertaken Reply: NFV reserved load reading undertaken 25/07/2023 Reply: NFV reserved load review undertaken Reply: NFV Load review undertaken 11/12/23
Note on V59: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Max usable tech load fig used as this is lower than the deployed capability
Note on AB64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on recorded readings as per forecasting spreadsheet Reply: NFV loads reviewed 20/04/2022 Reply: NFV reserved loads updated on 26/07/2022 Reply: NFV reserved loads updated on 23/12/2022 Reply: NFV reserved loads updated on 23/12/2023
Note on D70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last load reading date TBC
Note on E70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last load reading date TBC
Note on D71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last load reading date TBC
Note on E71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Last load reading date TBC
Note on AB73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: NFV reserved loads updated & Synergy frames capacity reduced from 7.5kW to 6kW on 26/08/2022 Reply: NFV reserved loads updated 29/12/2022 Reply: NFV reserved loads updated Reply: NFV Load updated on 29th July 23 Reply: NFV live & reserved loads updated 30/08/2023 Reply: NFV reserved loads updated 12/12/23
Note on H75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Number of modules reduced to 28 to move capacity onto DCSYS07a & b Reply: Following Eaton Upgrade revised rectifier count is 34
Note on AG76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 138A allocated (1.5kW per cab on day one, could go to 5kW) Reply: AP Reduced to 4 kW to be in line for the Network sites
Note on AE77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 138A allocated (1.5kW per cab on day one, could go to 5kW) Reply: AP Reduced to 4 kW to be in line for the Network sites
Note on W78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pending expansion of x5 rectifiers Reply: upgrade completed
Note on W79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pending expansion of x5 rectifiers
Note on AD86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No kit in cabs yet
Note on AD87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No kit in cabs yet
Note on D88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Possible controller failure 27/12/23
Note on AE94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 65A allocated
Note on AE95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 65A allocated
Note on B96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 85A increase on 19/08/22. Likely to be Redstream Evo RA, though no increase on PEDCF 05/9/22- 48A decrease 12/09/22- 26A decrease 26/09/22- 33A increase 03/10/22- 16A decrease 17/10/22- 24A increase 12/12/22- 100A decrease
Note on AG99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.5kW per cab on day one, could go to 5kW Reply: AP Reduced to 4 kW to be in line for the Network sites
Note on AI99: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced to 13A after M-CE upgrade completed
Note on AG100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1.5kW per cab on day one, could go to 5kW Reply: AP Reduced to 4 kW to be in line for the Network sites
Note on D109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take Reading from Rectifier Group - Total Current This follows on from its extension. Total load= sw rm 3 use (plus conversion DC-AC, remainder sw rm 1) Reply: Last load reading date 11/09/23
Note on E109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take Reading from Rectifier Group - Total Current This follows on from its extension. Total load= sw rm 3 use (plus conversion DC-AC, remainder sw rm 1) Reply: Last load reading date 11/09/23
Note on D112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take Reading from Rectifier Group - Total Current This follows on from its extension. Reply: Last load reading date 11/09/23
Note on E112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take Reading from Rectifier Group - Total Current This follows on from its extension. Reply: Last load reading date 11/09/23
Note on AD112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No kit in cabs yet
Note on AD113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No kit in cabs yet
Note on B133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: XCY currently manually added as 42

## WIP - Modelling Worksheet
MTX | (Multiple Items)
Row Labels | Sum of Element Load (A) Jan 21 | Sum of Running % load | Sum of Reserved (A) | Sum of Running Load + Reserved (%) | Sum of Forcast (A) | Sum of Total Forecast (kW) | Sum of Running Load + Reserved+ Forecast (A) | Sum of Total Power Element RAG (% used)
PECCF | 400 | 38.28% | 76 |  |  |  | 476 | 45.55%
PEDCF | 222 | 43.27% | 80 |  |  |  | 302 | 58.87%
PEECF | 350 | 68.23% | 0 |  |  |  | 350 | 68.23%
PEFBL | 510 | 48.8% | 68 |  |  |  | 578 | 55.31%
PEHBL | 390 | 37.32% | 68 |  |  |  | 458 | 43.83%

## Inverter Loading
MTX | Power Element Name | Power Element Type | Total Number of Inverters | Redundant inverters | Inverter Module Capacity (kW) | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | Available Capability (A) | Element Load (A) | Load Reading Date | Element Load (kW) | Total Load on DC power plants (A) | Total Load on DC power plants (kW) | Inverter Reserved Load (A) | Inverter Reserved Load (kW) | Forecast Load (A) | Forecast Load (kW) | Element Load+Reserved+Forecast (A) | Remaining Element Capability (A) | Power Element Remaining (RAG) | Forecasted elements (A) | Value (A) to be added to DC Power Plants
XAN | IC30aAN | ECI | 19 | 2 | 2.4 | 40.8 | 177 | 16.8 | 88.5 | 64 | 2024-01-21 | 15 | 300 | 16.35 | 8 | 1.84 | 2.5 | 0.575 | 74.5 | 14 | 15.82% | SecureNet (2.5A) | Originally 63A for cage.
XAN | IC30bAN | ECI | 19 | 2 | 2.4 | 40.8 | 177 | 16.8 | 88.5 | 55 | 2024-01-21 | 13 | 260 | 14.17 | 10 | 2.3 | 2.5 | 0.575 | 67.5 | 21 | 23.73% | SecureNet (2.5A) | Originally 63A for cage.
XBE | IC30aBE | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 71 | 2024-01-21 | 17 | 340 | 18.53 |  |  | 0 | 0 | 71 | 54 | 43.2%
XBE | IC30bBE | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 68 | 2024-01-21 | 16 | 320 | 17.44 |  |  | 0 | 0 | 68 | 57 | 45.6%
XBE | IC31aBE | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 66 | 2024-01-21 | 16 | 320 | 17.44 |  |  | 0 | 0 | 66 | 59 | 47.2%
XBE | IC31bBE | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 58 | 2024-01-21 | 14 | 280 | 15.26 |  |  | 0 | 0 | 58 | 67 | 53.6%
XBE | IC32aBE | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 24 | 2024-01-29 | 6 | 120 | 6.54 |  |  | 0 | 0 | 24 | 28 | 53.85%
XBE | IC32bBE | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 23 | 2023-04-14 | 6 | 120 | 6.54 |  |  | 0 | 0 | 23 | 29 | 55.77%
XCY | IC30aCY | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 33 | 2024-02-25 | 8 | 160 | 8.72 |  |  | 0 | 0 | 33 | 19 | 36.54% | SPARC T8-2 (13A)
XCY | IC30bCY | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 32 | 2024-02-25 | 8 | 160 | 8.72 |  |  | 0 | 0 | 32 | 20 | 38.46%
XEH | IC30aEH | ECI | 22 | 2 | 2.4 | 48 | 208 | 9.6 | 104 | 71 | 2024-01-21 | 17 | 340 | 18.53 |  |  | 3.3 | 0.759 | 74.3 | 29.7 | 28.56% | IPAR (3.3) | IPAR (14)
XEH | IC30bEH | ECI | 22 | 2 | 2.4 | 48 | 208 | 9.6 | 104 | 69 | 2024-01-21 | 16 | 320 | 17.44 |  |  | 3.3 | 0.759 | 72.3 | 31.7 | 30.48% | IPAR (3.3) | IPAR (14)
XER | IC30aER | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 15 | TBC | 4 | 80 | 4.36 |  |  | 0 | 0 | 15 | 37 | 71.15%
XER | IC30bER | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 11 | 2024-02-25 | 3 | 60 | 3.27 |  |  | 0 | 0 | 11 | 41 | 78.85%
XGL | IC30aGL | ECI | 21 | 2 | 2.4 | 45.6 | 198 | 21.6 | 99 | 52 | 2024-02-25 | 12 | 240 | 13.08 |  |  | 6 | 1.38 | 58 | 41 | 41.41% | Util AC03 (6) | Util AC03 (8)
XGL | IC30bGL | ECI | 21 | 2 | 2.4 | 45.6 | 198 | 21.6 | 99 | 43 | 2024-01-21 | 10 | 200 | 10.9 |  |  | 6 | 1.38 | 49 | 50 | 50.51% | Util AC03 (6) | Util AC03 (8)
XGL | IC31aGL | ECI | 21 | 2 | 2.4 | 45.6 | 198 | 21.6 | 99 | 44 | 2024-02-04 | 11 | 220 | 11.99 |  |  | 2.5 | 0.575 | 46.5 | 52.5 | 53.03% | SecureNet (2.5A) | SecureNet 11A
XGL | IC31bGL | ECI | 21 | 2 | 2.4 | 45.6 | 198 | 21.6 | 99 | 47 | 2024-02-25 | 11 | 220 | 11.99 |  |  | 2.5 | 0.575 | 49.5 | 49.5 | 50% | SecureNet (2.5A) | SecureNet 11A
XGR | IC30aGR | ECI | 14 | 2 | 2.4 | 28.8 | 125 | 0 | 62.5 | 15 | 2024-01-21 | 3.45 | 69 | 3.7605 |  |  | 10.8 | 2.484 | 25.8 | 36.7 | 58.72% | (Hawk 4.8) NFV Dell Store (6) | Hawk (21A) NFV Dell Store (6.4)
XGR | IC30bGR | ECI | 14 | 2 | 2.4 | 28.8 | 125 | 0 | 62.5 | 13 | 2024-01-21 | 2.99 | 59.8 | 3.2591 |  |  | 10.8 | 2.484 | 23.8 | 38.7 | 61.92% | (Hawk 4.8) NFV Dell Store (6) | Hawk (21A) NFV Dell Store (6.4)
XGR | GCRMTX-INV02a | ECI | 14 | 2 | 2.4 | 28.8 | 125 | 0 | 62.5 | 41.6 | 2023-04-03 | 11.8 | 236 | 12.862 |  |  | 3.5 | 0.805 | 45.1 | 17.4 | 27.84% | HPE Store (0.5) Compute 421 (3A)
XGR | GCRMTX-INV02b | ECI | 14 | 2 | 2.4 | 28.8 | 125 | 0 | 62.5 | 41.2 | 2023-04-03 | 11.8 | 236 | 12.862 |  |  | 3.5 | 0.805 | 44.7 | 17.8 | 28.48% | HPE Store (0.5) Compute 421 (3A)
XKS | IC30aKS | ECI | 24 | 2 | 2.4 | 52.8 | 229 | 4.8 | 114.5 | 83 | 2024-02-25 | 20 | 400 | 21.8 |  |  | 0 | 0 | 83 | 31.5 | 27.51%
XKS | IC30bKS | ECI | 24 | 2 | 2.4 | 52.8 | 229 | 4.8 | 114.5 | 77 | 2024-02-25 | 18 | 360 | 19.62 |  |  | 0 | 0 | 77 | 37.5 | 32.75%
XLD | IC30aLD | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 92 | 2023-10-15 | 22 | 440 | 23.98 |  |  | 10 | 2.3 | 102 | 23 | 18.4% | 23016 NFV CV 101 (10A) | Net 103 (22.6A)
XLD | IC30bLD | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 99 | 2024-02-25 | 23 | 460 | 25.07 |  |  | 10 | 2.3 | 109 | 16 | 12.8% | 23016 NFV CV 101 (10A) | Net 103 (22.6A)
XMS | IC20aMS | TSI | 21 | 6 | 2 | 30 | 130 | 18 |  | 23 | TBC | 6 | 120 | 6.54 |  |  | 0 | 0 | 23 | 107
XMS | IC20bMS | TSI | 21 | 6 | 2 | 30 | 130 | 18 |  | 23 | TBC | 6 | 120 | 6.54 |  |  | 0 | 0 | 23 | 107
XMS | IC30aMS | ECI | 19 | 2 | 2.4 | 40.8 | 177 | 26.4 | 88.5 | 64 | 2024-01-21 | 15 | 300 | 16.35 |  |  | 0 | 0 | 64 | 24.5 | 27.68%
XMS | IC30bMS | ECI | 19 | 2 | 2.4 | 40.8 | 177 | 26.4 | 88.5 | 62 | 2024-01-21 | 15 | 300 | 16.35 |  |  | 0 | 0 | 62 | 26.5 | 29.94%
XMS | IC31aMS | ECI | 25 | 2 | 2.4 | 55.2 | 240 | 12 | 120 | 50 | 2024-01-21 | 12 | 240 | 13.08 |  |  | 0 | 0 | 50 | 70 | 58.33%
XMS | IC31bMS | ECI | 25 | 2 | 2.4 | 55.2 | 240 | 12 | 120 | 50 | 2024-01-21 | 12 | 240 | 13.08 |  |  | 0 | 0 | 50 | 70 | 58.33%
XOM | IC30aOM | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 109 | 2024-02-04 | 26 | 520 | 28.34 |  |  | 4.8 | 1.104 | 113.8 | 11.2 | 8.96% | (Hawk 4.8) | Hawk (21A)
XOM | IC30bOM | ECI | 26 | 2 | 2.4 | 57.6 | 250 | 0 | 125 | 107 | 2023-11-19 | 25 | 500 | 27.25 |  |  | 4.8 | 1.104 | 111.8 | 13.2 | 10.56% | (Hawk 4.8) | Hawk (21A)
XRM | IC30aRM | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 19 | 2024-01-07 | 5 | 100 | 5.45 |  |  |  | 0 | 19 | 33 | 63.46%
XRM | IC30bRM | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 12 | 2024-01-21 | 3 | 60 | 3.27 |  |  | 0 | 0 | 12 | 40 | 76.92%
XSN | IC30aSN | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 14 | 2024-01-21 | 4 | 80 | 4.36 |  |  | 0 | 0 | 14 | 38 | 73.08%
XSN | IC30bSN | ECI | 12 | 2 | 2.4 | 24 | 104 | 33.6 | 52 | 11 | 2024-01-21 | 3 | 60 | 3.27 |  |  | 0 | 0 | 11 | 41 | 78.85%
XSY | IC30aSY | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 16 | 2024-01-21 | 4 | 80 | 4.36 |  |  | 0 | 0 | 16 | 36 | 69.23%
XSY | IC30bSY | ECI | 12 | 2 | 2.4 | 24 | 104 | 4.8 | 52 | 12 | 2024-02-25 | 3 | 60 | 3.27 |  |  | 0 | 0 | 12 | 40 | 76.92%
Note- the inverter systems readings are greater than the PDU readings, this is due to the CT (current transformers) used for circuit monitoring. The inverter system reading is used for Dulux.
MTX | Name | Type | Total Number of Inverters | Redundant inverters | Inverter Module Capacity (kW) | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | Available Capability (A) | Element Load (A) | Load Reading Date | Element Load (kW) | Total Load on DC power plants (A) | Total Load on DC power plants (kW) | Inverter Reserved Load (A) | Reserved Load (kW) | Forecast Load (A) | Forecast Load (kW) | Element Load+Reserved+Forecast (A) | Remaining Element Capability (A) | Power Element Remaining (RAG) | Forecasted elements | Value (A) to be added to each DC Power Plant
XBL | IC2BL | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 5 | 2024-02-25 | 1.15 | 23 | 1.2535 |  |  | 0 | 0 | 5 | 36 | 0.87805
XCF | IC2CF | RDI | 6 | 3 | 3 | 9 | 39 | 33 | 39 | 1 | TBC | 0.23 | 4.6 | 0.2507 |  |  | 0 | 0 | 1 | 38 | 0.97436
XCE | IC2CE | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 5 | 2024-02-25 | 1.15 | 23 | 1.2535 |  |  | 0 | 0 | 5 | 36 | 0.87805
XCN | IC3CN | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 8 | 2024-02-25 | 1.84 | 36.8 | 2.0056 |  |  | 0 | 0 | 8 | 33 | 0.80488
TGW | IC1GW | TSI | 3 | 1 | 0.525 | 1.05 | 4 | 0 | 4 | 2 | 2024-02-25 | 0.46 | 9.2 | 0.5014 |  |  | 0 | 0 | 2 | 2 | 0.5
XLR | IC3LR | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 7 | 2024-02-25 | 1.61 | 32.2 | 1.7549 |  |  | 0 | 0 | 7 | 34 | 0.82927
XNE | IC3NE | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 6 | 2024-02-25 | 1.38 | 27.6 | 1.5042 |  |  | 0 | 0 | 6 | 35 | 0.85366
XNY | IC4NY | ECI | 8 | 2 | 2.4 | 14.4 | 62 | 27.6 | 62 | 41 | TBC | 9.43 | 188.6 | 10.2787 |  |  | 0 | 0 | 41 | 21 | 0.33871
XNY | Canal House UPS | UPS | 2 | 1 | 75 | 75 | 326 | 0 | 326 | 172 | 2023-09-10 | 39 |  |  |  |  | 8 | 1.84 | 180 | 146 | 0.44785 | PE Increases
XOD | IC2OD | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 5 | 2024-02-25 | 1.15 | 23 | 1.2535 |  |  | 0 | 0 | 5 | 36 | 0.87805
XSD | IC3SD | ECI | 6 | 2 | 2.4 | 9.6 | 41 | 32.4 | 41 | 7 | 2024-02-25 | 1.61 | 32.2 | 1.7549 |  |  | 0 | 0 | 7 | 34 | 0.82927
TWN | IC3WN | TSI | 3 | 1 | 2 | 4 | 17 | 0 | 17 | 3 | 2024-02-25 | 0.69 | 0 | 0 |  |  | 0 | 0 | 3 | 14 | 0.82353
XER | IC2ER | RDI | 8 | 3 | 3 | 15 | 65 | 27 | 10 | 3 | 3.27 |  | 0 | 0
Type A - Reporting Data
Name | System Load (kW) | Reserved (kW) | Forecast (kW) | Deployed Capacity (kW) |  | Power Capability (kW) | Power Element RAG (% remaining)
IC30AN | 28 | 16 | 0.575 | -3.775 |  | 16.8 | -9.252%
IC30BE | 33 | 0 | 0 | 24.6 |  | 0 | 42.71%
IC31BE | 30 | 0 | 0 | 27.6 |  | 0 | 47.92%
IC30CY | 16 | 0 | 0 | 8 |  | 4.8 | 33.33%
#REF! | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC13GL | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC14GL | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC30GL | 22 | 0 | 2.76 | 20.84 |  | 21.6 | 45.7%
IC31GL | 22 | 0 | 1.15 | 22.45 |  | 21.6 | 49.23%
IC30GR | 6.44 | 0 | 4.968 | 17.392 |  | 0 | 60.39%
IC30KS | 38 | 0 | 0 | 14.8 |  | 2.4 | 28.03%
IC12LD | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC13LD | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC30LD | 45 | 0 | 4.6 | 8 |  | 0 | 13.89%
IC20MS | 12 |  | 0 | 18 |  | 18 | 60%
IC30MS | 30 | 0 | 0 | 10.8 |  | 26.4 | 26.47%
IC31MS | 24 | 0 | 0 | 31.2 |  | 12 | 56.52%
IC30OM | 51 | 0 | 2.208 | 4.392 |  | 0 | 7.625%
IC30RM | 8 | 0 | 0 | 16 |  | 4.8 | 66.67%
#REF! | #REF! |  | #REF! | #REF! |  | #REF! | #REF!
IC30SY | 7 | 0 | 0 | 17 |  | 4.8 | 70.83%
Core Graphing data
Name | System Load (kW) | Forecast (kW) | Deployed Capacity (kW) | Power Capability (kW)
ICxBE | 63 | 0 | 52.2 | 0
ICxGL | 44 | 3.91 | 43.29 | 43.2
ICxLD | 45 | 4.6 | 8 | 0
ICxMS | 54 | 0 | 42 | 38.4
Type B Graphing data
Name | System Load (kW) | Forecast (kW) | Deployed Capacity (kW) | Power Capability (kW)
IC2BL | 1.15 | 0 | 8.45 | 32.4
IC2CE | 1.15 | 0 | 8.45 | 32.4
IC2CF | 0.23 | 0 | 8.77 | 33
IC3CN | 1.84 | 0 | 7.76 | 32.4
IC1GW | 0.46 | 0 | 0.59 | 0
#REF! | #REF! | #REF! | #REF! | #REF!
IC3LR | 1.61 | 0 | 7.99 | 32.4
IC3LS | #REF! | #REF! | #REF! | #REF!
IC3NE | 1.38 | 0 | 8.22 | 32.4
IC4NY | 9.43 | 0 | 4.97 | 27.6
IC2OD | 1.15 | 0 | 8.45 | 32.4
IC3SD | 1.61 | 0 | 7.99 | 32.4
IC3WN | 0.69 | 0 | 3.31 | 0
IC1WY | #REF! | #REF! | #REF! | #REF!
| 39 | 1.84 | 34.16 | 0
CH PDU | System Load (A) | Forecast (A) | Remaining Capacity (A) | [18 empty] | CH PDU Forecasted Elements
Phase L1 | 70 | 2 | 58 | [18 empty] | 2A (VFPTSP 22015)
Phase L2 | 48 | 0 | 82
Phase L3 | 61 | 0 | 69
Total (A) | 179
Total(kW) | 42
Max load on PDU 75kW (130A per phase limit)
Note on X1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Value (W)/54.5/No of plants feeding AC plant then add 10% for losses
Note on P2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Security Cage
Note on B20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: a and b side to be viewed as single system
Note on D20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inc from 12 to 14 Jan 21
Note on B21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: a and b side to be viewed as single system
Note on D21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inc from 12 to 14 Jan 21
Note on W22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: VFPTSP 22005. 12A allocated, 4A reduction to match XOM
Note on K28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load from PRISM
Note on K29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Load from PRISM
Note on D30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x3 more connected not used
Note on D31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x3 more connected not used
Note on B52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Max load on PDU 75kW/ 94kVA, max 130A per phase,
Note on D52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Figures for GIS migration only
Note on E52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Figures for GIS migration only
Note on F52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Figures for GIS migration only
Note on M52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Refer to AxScada
Note on C62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Security cage has max allocatoin of 20kW. 11/12/17 Cage has 16kW remaining
Note on D112: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: (130A per phase) Max 75kW on PDU https://axscada.ad.plc.cwintra.com/login pmc

## Plant Loading Property Report
DC Power Plant Usage Report
Type A Sites
| MTX | Technology Load for the site (kW) | Reserved+Forecast for the site (kW) | Deployed DC Capability (kW) | Max Technology Load (kW)
| XAN | 173.528 | 15.4235 | 315 | 315
| XBE | 372.671 | 96.6285 | 504 | 504 |  |  | Kings Cross Breakdown
| XCY | 126.44 | 8.066 | 315 | 315 |  | MTX | DC Load for the site (kW) | Forecast for the site (kW) | Deployed DC Capability (kW) | Max Technology Load (kW)
| XEH | 285.6345 | 71.504 | 378 | 378 |  | XKS - 1st Floor | 38.15 | 0 | 115.5 | 120
| XER | 83.0035 | 0 | 252 | 300 |  | XKS - 2nd Floor | 67.6345 | 0 | 178.5 | 120
| XGR | 260.183 | 151.4119 | 468 | 465 |  | XKS - 3rd Floor | 21.691 | 0 | 105 | 120
| XGL | 295.172 | 87.696 | 477 | 480
| XKS | 127.4755 | 0 | 399 | 483
| XLD | 331.251 | 63.002 | 501 | 478
| XMS | 367.766 | 74.8285 | 483 | 480
| XOM | 293.21 | 121.8075 | 489 | 473
| XRM | 100.2255 | 14.715 | 315 | 315
| XSN | 95.3205 | 18.748 | 252 | 300
| XSY | 111.7795 | 0 | 304.5 | 304.5
Type B Sites
| MTX | Technology Load for the site (kW) | Reserved+Forecast for the site (kW) | Deployed DC Capability (kW) | Max Technology Load (kW)
| XBL | 43.8725 | 5.0685 | 115 | N/A
| XCF | 39.6215 | 4.796 | 115 | N/A
| XCE | 45.998 | 14.606 | 114.5 | N/A
| XCN | 38.15 | 4.796 | 115 | N/A
| TGW | 9.374 | 0 | 31 | N/A
| XLR | 62.457 | 0 | 115 | N/A
| XNY | 37.06 | 0 | 115 | N/A
| XNE | 44.472 | 8.611 | 143.5 | N/A
| XOD | 20.383 | 11.663 | 105.5 | N/A
| XSD | 44.1995 | 0 | 115 | N/A
| TWN | 39.567 | 0 | 85.5 | N/A
Power Element Name | Power Element Type | Power Plant Load (kW) | Reserved+Forecast (kW) | Number of Modules | Module Capacity (kW) | Useable Power Capacity (kW) | Total Power Plant Capacity (kW)
PEAAN | eSure | 34.2805 | 3.2155 | 36 | 3.5 | 63 | 126
PEBAN | eSure | 33.8445 | 3.4335 | 36 | 3.5 | 63 | 126
PECAN | eSure | 25.179 | 2.8885 | 36 | 3.5 | 63 | 126
PEFAN | eSure | 38.8585 | 2.725 | 36 | 3.5 | 63 | 126
PEGAN | eSure | 41.3655 | 3.161 | 36 | 3.5 | 63 | 126
PEABE | eSure | 44.472 | 8.5292 | 36 | 3.5 | 63 | 126
PEBBE | eSure | 45.78 | 13.298 | 36 | 3.5 | 63 | 126
PECBE | eSure | 44.0905 | 9.81 | 36 | 3.5 | 63 | 126
PEEBE | eSure | 47.3605 | 11.0907 | 36 | 3.5 | 63 | 126
PEFBE | eSure | 46.1615 | 17.7125 | 36 | 3.5 | 63 | 126
PEGBE | eSure | 47.851 | 12.1535 | 36 | 3.5 | 63 | 126
PEHBE | eSure | 47.524 | 11.663 | 36 | 3.5 | 63 | 126
PEIBE | eSure | 49.4315 | 12.3715 | 36 | 3.5 | 63 | 126
PEACY | eSure | 21.3095 | 0.8175 | 36 | 3.5 | 63 | 126
PEBCY | eSure | 27.0865 | 0.8175 | 36 | 3.5 | 63 | 126
PECCY | eSure | 33.1905 | 0.8175 | 36 | 3.5 | 63 | 126
PEDCY | eSure | 25.724 | 3.2155 | 36 | 3.5 | 63 | 126
PEECY | eSure | 19.1295 | 2.398 | 36 | 3.5 | 63 | 126
PECEH | eSure | 45.562 | 12.6713 | 36 | 3.5 | 63 | 126
PEDEH | eSure | 48.9955 | 10.5457 | 36 | 3.5 | 63 | 126
PEEEH | eSure | 47.1425 | 11.4177 | 36 | 3.5 | 63 | 126
PEFEH | eSure | 44.908 | 11.0363 | 36 | 3.5 | 63 | 126
PEGEH | eSure | 51.448 | 10.5457 | 36 | 3.5 | 63 | 126
PEHEH | eSure | 47.5785 | 15.2873 | 36 | 3.5 | 63 | 126
PEDER | eSure | 22.6175 | 0 | 36 | 3.5 | 63 | 126
PEEER | eSure | 20.2195 | 0 | 36 | 3.5 | 63 | 126
PEFER | eSure | 23.217 | 0 | 36 | 3.5 | 63 | 126
PEGER | eSure | 16.9495 | 0 | 36 | 3.5 | 63 | 126
PEAGR | eSure | 34.9345 | 10.6111 | 36 | 3.5 | 63 | 126
PEBGR | eSure | 41.6925 | 10.6111 | 36 | 3.5 | 63 | 126
PECGR | eSure | 39.022 | 40.8041 | 36 | 3.5 | 63 | 126
PEDGR | eSure | 38.7495 | 14.3716 | 36 | 3.5 | 63 | 126
PEEGR | eSure | 38.4225 | 11.9355 | 36 | 3.5 | 63 | 126
GCRMTX-DCSYS06a | NPR48-ES | 34.8255 | 30.2857 | 51 | 3 | 75 | 153
GCRMTX-DCSYS06b | NPR48-ES | 32.5365 | 32.7927 | 51 | 3 | 75 | 153
BMGMTX-DCSYS01 | HDR48-ES | 41.747 | 4.033 | 44 | 3 | 63 | 132
BMGMTX-DCSYS02 | HDR48-ES | 42.7825 | 5.6135 | 44 | 3 | 63 | 132
PECGL | eSure | 46.761 | 9.7555 | 36 | 3.5 | 63 | 126
BMGMTX-DCSYS04 | HDR48-ES | 43.4365 | 9.2105 | 44 | 3 | 63 | 132
BMGMTX-DCSYS05 | HDR48-ES | 43.5455 | 6.213 | 44 | 3 | 63 | 132
PEFGL | eSure | 45.998 | 10.7365 | 36 | 3.5 | 63 | 126
BMGMTX-DCSYS07a | NPR48-ES | 15.478 | 21.0588 | 29 | 3 | 42 | 87
BMGMTX-DCSYS07b | NPR48-ES | 15.4235 | 21.0752 | 29 | 3 | 42 | 87
PEAKS | eSure | 13.516 | 0 | 24 | 3.5 | 42 | 84
PEBKS | eSure | 19.184 | 0 | 30 | 3.5 | 52 | 105
PEEKS | eSure | 5.45 | 0 | 12 | 3.5 | 21 | 42
PEIKS | eSure | 28.776 | 0 | 36 | 3.5 | 63 | 126
PEJKS | eSure | 12.4805 | 0 | 36 | 3.5 | 63 | 126
PEKKS | eSure | 26.378 | 0 | 30 | 3.5 | 52 | 105
PELKS | eSure | 8.7745 | 0 | 24 | 3.5 | 42 | 84
PEMKS | eSure | 7.957 | 0 | 24 | 3.5 | 42 | 84
PENKS | eSure | 4.9595 | 0 | 12 | 3.5 | 21 | 42
LLDMTX-DCSYS01 | HDR48-ES | 49.1045 | 6.3765 | 44 | 3 | 63 | 132
LLDMTX-DCSYS02 | HDR48-ES | 44.145 | 7.63 | 44 | 3 | 63 | 132
LLDMTX-DCSYS03 | HDR48-ES | 50.6305 | 5.5045 | 44 | 3 | 63 | 132
LLDMTX-DCSYS04 | HDR48-ES | 46.8155 | 3.9785 | 44 | 3 | 63 | 132
LLDMTX-DCSYS05 | HDR48-ES | 49.595 | 4.687 | 44 | 3 | 63 | 132
LLDMTX-DCSYS06 | HDR48-ES | 48.941 | 4.142 | 44 | 3 | 63 | 132
LLDMTX-DCSYS07a | NPR48-ES | 20.9825 | 15.369 | 35 | 3 | 51 | 105
LLDMTX-DCSYS07b | NPR48-ES | 21.037 | 15.3145 | 35 | 3 | 51 | 105
PEAMS | eSure | 57.007 | 13.1617 | 42 | 3.5 | 73 | 147
PEBMS | eSure | 53.846 | 12.9165 | 42 | 3.5 | 73 | 147
PECMS | eSure | 52.32 | 16.1593 | 42 | 3.5 | 73 | 147
PEDMS | eSure | 61.6395 | 9.3195 | 42 | 3.5 | 73 | 147
PEEMS | eSure | 57.2795 | 6.2675 | 42 | 3.5 | 73 | 147
PEFMS | eSure | 56.9525 | 7.957 | 42 | 3.5 | 73 | 147
DCSYS07A | NPR48-ES | 14.2245 | 4.5235 | 16 | 3 | 21 | 48
DCSYS07B | NPR48-ES | 14.497 | 4.5235 | 16 | 3 | 21 | 48
OLDMTX-DCSYS01 | HDR48-ES | 48.3415 | 8.7745 | 44 | 3 | 63 | 132
OLDMTX-DCSYS02 | HDR48-ES | 44.581 | 12.1535 | 44 | 3 | 63 | 132
OLDMTX-DCSYS03 | HDR48-ES | 44.69 | 11.118 | 44 | 3 | 63 | 132
OLDMTX-DCSYS04 | HDR48-ES | 33.5175 | 10.791 | 34 | 3 | 48 | 102
OLDMTX-DCSYS05 | HDR48-ES | 34.7165 | 16.241 | 44 | 3 | 63 | 132
OLDMTX-DCSYS06 | HDR48-ES | 35.534 | 15.042 | 44 | 3 | 63 | 132
OLDMTX-DCSYS07a | NPR48-ES | 26.16 | 22.781 | 36 | 3 | 51 | 108
OLDMTX-DCSYS07b | NPR48-ES | 25.6695 | 24.9065 | 36 | 3 | 51 | 108
PEARM | eSure | 21.8545 | 0 | 36 | 3.5 | 63 | 126
PEBRM | eSure | 23.8165 | 3.5425 | 36 | 3.5 | 63 | 126
PECRM | eSure | 29.0485 | 3.5425 | 36 | 3.5 | 63 | 126
PEDRM | eSure | 13.952 | 3.815 | 36 | 3.5 | 63 | 126
PEERM | eSure | 11.554 | 3.815 | 36 | 3.5 | 63 | 126
PEASN | eSure | 20.056 | 0 | 36 | 3.5 | 63 | 126
PEBSN | eSure | 29.648 | 9.374 | 36 | 3.5 | 63 | 126
PECSN | eSure | 26.7595 | 9.374 | 36 | 3.5 | 63 | 126
PEESN | eSure | 18.857 | 0 | 36 | 3.5 | 63 | 126
PEASY | eSure | 29.321 | 0 | 36 | 3.5 | 63 | 126
PEBSY | eSure | 27.141 | 0 | 36 | 3.5 | 63 | 126
PECSY | eSure | 20.928 | 0 | 36 | 3.5 | 63 | 126
PEDSY | eSure | 16.241 | 0 | 36 | 3.5 | 63 | 126
PEESY | eSure | 18.1485 | 0 | 30 | 3.5 | 52 | 105
PEFBL | NetSure | 25.942 | 2.2345 | 36 | 3.2 | 57 | 115
PEHBL | NetSure | 17.9305 | 2.834 | 36 | 3.2 | 57 | 115
PECCF | NetSure | 19.184 | 2.398 | 36 | 3.2 | 57 | 115
PEDCF | NetSure | 8.9925 | 2.398 | 18 | 3.2 | 28 | 57
PEECF | NetSure | 11.445 | 0 | 18 | 3.2 | 28 | 57
PEACE | NetSure | 21.8 | 7.303 | 36 | 3.2 | 57 | 115
PEBCE | NetSure | 24.198 | 7.303 | 36 | 3.2 | 57 | 115
PEFCN | NetSure | 17.0585 | 2.398 | 36 | 3.2 | 57 | 115
PEGCN | NetSure | 21.0915 | 2.398 | 36 | 3.2 | 57 | 115
PEJGW | eSure | 4.7415 | 0 | 9 | 3.5 | 21 | 31
PEKGW | eSure | 4.6325 | 0 | 9 | 3.5 | 21 | 31
PEFLR | NetSure | 34.117 | 0 | 36 | 3.2 | 57 | 115
PEGLR | NetSure | 28.34 | 0 | 36 | 3.2 | 57 | 115
PEGNY | NetSure | 19.947 | 0 | 36 | 3.2 | 57 | 115
PEHNY | NetSure | 17.113 | 0 | 36 | 3.2 | 57 | 115
PEENE | NetSure | 16.677 | 3.2155 | 36 | 3.2 | 57 | 115
PEFNE | NetSure | 19.5655 | 4.3055 | 36 | 3.2 | 57 | 115
PEGNE | NetSure | 8.2295 | 1.09 | 18 | 3.2 | 28 | 57
PECOD | NetSure | 12.862 | 5.8315 | 36 | 3.2 | 57 | 115
PEFOD | NetSure | 7.521 | 5.8315 | 30 | 3.2 | 48 | 96
PEESD | NetSure | 21.473 | 0 | 36 | 3.2 | 57 | 115
PEGSD | NetSure | 22.7265 | 0 | 36 | 3.2 | 57 | 115
PELWN | NetSure | 11.3905 | 0 | 18 | 3.2 | 28 | 57
PEMWN | NetSure | 8.502 | 0 | 18 | 3.2 | 28 | 57
PENWN | NetSure | 19.6745 | 0 | 18 | 3.2 | 28 | 57

## NFV
(to 90% Capacity Mgmt Limit)
| Site | 100% Capacity kW | 90% Maximum Capacity Management Limit | 10% Cap Mgmt Limit | Running Load kW | NFV Reserved kW | Forecast kW | Run Load + Fore +Res | Remaining Capacity kW | Remaining kW including NFV Reserve | Maximum NFV Require FY22-23 kW | Typical NFV Require FY22-23 kW | Remaining kW (to 100% Capacity) | Original Forecast kW | 85% Figure | Remaining Cap kW to 85% | 80% |  | Typical/Max Demand | Hardware Name | OEM Requested Max (kW) | NDI Reserve (kW) | NDI Reserve/OEM Requested
| XOM | 464.6125 | 418.1512 | 46.4612 | 293.21 | 105.5665 | 16.241 | 415.0175 | 3.1337 | 108.7002 | Dell S5248F | Dell S5248F | 49.595 |  | 394.9206 | -20.0969 | 371.69 | -43.3275 | #VALUE! | Gen 9 HP | 6.5 | 5 | 76.92%
| XGL | 461.615 | 415.4535 | 46.1615 | 295.172 | 67.3075 | 20.3884 | 382.868 | 32.5855 | 99.893 | Dell S5248F | Dell S5248F | 78.747 |  | 392.3727 | 9.5048 | 369.292 | -13.576 | #VALUE! | Gen 10 HPC | 7.5 | 5 | 66.67%
| XGR | 464.7215 | 418.2493 | 46.4721 | 260.183 | 119.8455 | 31.5664 | 411.5949 | 6.6544 | 126.4999 | Dell S5248F | Dell S5248F | 53.1266 |  | 395.0133 | -16.5816 | 371.7772 | -39.8177 | #VALUE! | Dell M1000e | 6.5 | 4.5 | 69.23%
| XBE | 503.58 | 453.222 | 50.358 | 372.671 | 39.022 | 57.6065 | 469.2995 | -16.0775 | 22.9445 | Dell S5248F | Dell S5248F | 34.2805 |  | 428.043 | -41.2565 | 402.864 | -66.4355 | #VALUE! | Synergy AC | 10.5 | 6.5 | 61.9%
| XEH | 377.685 | 356.9123 | 22.6611 | 285.6345 | 65.1275 | 6.3765 | 357.1385 | -0.22618 | 64.9013 | Dell S5248F | Dell S5248F | 20.5465 |  | 321.0322 | -36.1063 | 302.148 | -54.9905 | #VALUE! | Synergy DC | 8.5 | 6 | 70.59%
| XMS | 479.818 | 431.8362 | 47.9818 | 367.766 | 28.7215 | 46.107 | 442.5945 | -10.7583 | 17.9632 | Dell S5248F | Dell S5248F | 37.2235 |  | 407.8453 | -34.7492 | 383.8544 | -58.7401 | #VALUE!
| XLD | 466.4125 | 419.7712 | 46.6412 | 331.251 | 55.917 | 7.085 | 394.253 | 25.5182 | 81.4352 | Dell S5248F | Dell S5248F | 72.1595 |  | 396.4506 | 2.1976 | 373.13 | -21.123 | #VALUE!
| BKL | 345 | 310.5 | 34.5 | 160 | 61 | 88 | 309 | 1.5 | 62.5 | Dell S5248F | Dell S5248F | 36 |  | 293.25 | -15.75 | 276 | -33 | #VALUE!
| RMS Cab type | OEM Max Value (KW) | OEM Typical Values (KW)
| Storage Cab Live ( 4 x Powerstore 500T, 2 x 5448 Storage Leaf Switches, 2 x 9432 Storage Spine Switches) | 7.35 | 4.74
| 8 X RMS Host and High Performance Networking ( 2 x 5448 Service TOR , 1 x 5448 Storage TOR , 1 x 5248 Mgmt TOR) | 9.15 | 5.84
| 8 X RMS Host and STD Performance Networking ( 1 x 5448 Service TOR , 1 x 5448 Storage TOR , 1 x 5248 Mgmt TOR) | 8.2 | 5.34
| 11 x RMS and 1 x 2248 OOB switch | 8.2 | 5.85
| 10 x RMS cab | 7.15 | 5.04
| Hi Perf POD Power Loads per POD Kw | Storage Kw | Site Totals |  | POD with x38 RMS
1 | 41.85 | 7.35 | 49.2 |  | 34.7
2 | 83.7
| STD Perf POD Power Loads per POD Kw | Storage Kw | Site Totals
1 | 39.95 | 7.35 | 47.3
2 | 79.9
| Site Requirements | Power Requirement | Remaining CAP kW to 85%
| XGR x1 Store, x2 High Perf RMS & x1 STD Perf RMS | 131 | 99.7 | x2 PODs & Storage cabinets 90kW
| XGL x1 Store, x2 High Perf RMS & x2 STD Perf RMS | 170.95 | Needs new room | DC capacity can be used for CISCO 9912
| XOM x1 Store, x2 High Perf RMS & x2 STD Perf RMS | 170.95 | 75 | x2 PODs & Storage cabinets 90kW or 83kW second POD with last cabinet empty so -10 RMS
| BKLN05 x1 Store, x1 High Perf RMS & x1 STD Perf RMS | 89.15 | 90 | If to 90% of UPS then can go into BKLN05 ext
Infra Ready - NDI [Cables & Cabs]134 daysTue 27/09/22Fri 31/03/23
XOM [19] Thu 26/01/23
XGL [28] [AC Room] Fri 31/03/23 Cabinet on site with power to undertake build
BKNL [21] Wed 30/11/22
XGR [15] Thu 26/01/23
Note on F10: Lee, Rich: Use 6% figure to ensure total adds to 100% as current utilisation is 94%
Note on K10: Lee, Rich: This is remaining capacity based on 94% utilisation as we have exceeded 90% capacity management limit
Note on D13: Lee, Richard.X, Vodafone: Combined AC & DC total DC = 190kW (80% of N) AC = 310kW AP AC only figures 345kW
Note on G13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note this figure taken from iPDU sheets not true running loads but are forecast loads . 160 running load is the 221kW less 61kW Reserved
Note on H13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Reserved figures is based on the live figures from the NFV Ops team
Note on R13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should this not be 90% for the AC in BKLN05?

## Cab Floorspace
Site Name | Total Eqpt Rm Area (m²) | Total Footprints (S) | Total Footprints (D)-after calc | Spare Footprints (S) | Spare Footprints (D)-after calc | Calc- Deep Cabs Tiles | Deep Cabs Footprints (based on 800mm Wide Cab) |  |  |  |  | Total Footprints (S)m2 | Total Footprints (D)-after calc | Standard Cab Footprints Spare | Deep Cab Footprints Spare-after calc
XAN | 943 | 326 | 96 | 190 | 27 | 37 | 27 |  |  |  |  | 452.64 | 260.8 | 46.08 | 152
XBE | 1614 | 586 | 261 | 327 | 106 | 142 | 106 |  |  |  |  | 774.72 | 468.8 | 125.28 | 261.6
XCY | 1073 | 611 | 83 | 444 | 24 | 33 | 24 |  |  |  |  | 515.04 | 488.8 | 39.84 | 355.2
XEH | 837 | 337 | 113 | 110 | 16 | 22 | 16 |  |  |  |  | 401.76 | 269.6 | 54.24 | 88
XER | 701 | 384 | 32 | 201 | 16 | 22 | 16 |  |  |  |  | 336.48 | 307.2 | 15.36 | 160.8
XGR | 1044 | 515 | 114 | 305 | 26 | 35 | 26 |  |  |  |  | 501.12 | 412 | 54.72 | 244
XGL | 1045 | 399 | 167 | 134 | 26 | 35 | 26 |  |  |  |  | 501.6 | 319.2 | 80.16 | 107.2
XKS (1st) | 619 | 302 | 39 | 171 | 19 | 26 | 19 |  |  |  |  | 297.12 | 241.6 | 18.72 | 136.8
XKS (2nd) | 621 | 273 | 39 | 148 | 1 | 2 | 1 |  |  |  |  | 298.08 | 218.4 | 18.72 | 118.4
XKS (3rd) | 622 | 240 | 30 | 195 | 24 | 41 | 30 |  |  |  |  | 298.56 | 192 | 14.4 | 156
XLD | 1049 | 453 | 127 | 171 | 28 | 38 | 28 |  |  |  |  | 503.52 | 362.4 | 60.96 | 136.8
XMS | 1045 | 386 | 208 | 188 | 35 | 47 | 35 |  |  |  |  | 501.6 | 308.8 | 99.84 | 150.4
XOM | 1415 | 536 | 117 | 357 | 47 | 53 | 39 |  |  |  |  | 679.2 | 428.8 | 56.16 | 285.6
XRM | 1078 | 595 | 63 | 379 | 21 | 29 | 21 |  |  |  |  | 517.44 | 476 | 30.24 | 303.2
XSN | 1218 | 666 | 57 | 521 | 15 | 76 | 57 |  |  |  |  | 584.64 | 532.8 | 27.36 | 416.8
XSY | 861 | 469 | 43 | 283 | 20 | 27 | 20 |  |  |  |  | 413.28 | 375.2 | 20.64 | 226.4
Graphing Calcs
NFV Sites
Site Name | Current Usage (S) | Reserved no of cabs (S) | Forecast no of cabs (S) | Remaining Capacity (S) | Current Usage (D) | Reserved no of cabs (D) | Forecast no of cabs (D) | Remaining Capacity (D) | Used (m²) | Reserved (m²) | Forecast (m²) | Total usable space (m²) (based on cab positions and front/back space) | % usable space remaining | Remaining (m²) |  | % usable space remaining
XBE | 1353 | 0 | 0 | 261 | 259 | 1 | 8 | 318 | 1713.28 | 1.6 | 12.8 | 2487.04 | 31.11% | 759.36 |  | 44.41% | 100% | 55.59%
XMS | 837 | 2 | 6 | 200 | 198 | 0 | 6 | 182 | 1120.32 | 1.92 | 15.36 | 1620.8 | 30.88% | 483.2 |  | 22.02% | 100% | 77.98%
XLD | 922 | 16 | 0 | 111 | 282 | 3 | 0 | 168 | 1336.32 | 20.16 | 0 | 1731.84 | 22.84% | 375.36 |  | 35.54% | 100% | 64.46%
XEH | 724 | 6 | 4 | 103 | 227 | 1 | 0 | 109 | 1058.24 | 7.36 | 3.84 | 1342.72 | 21.19% | 273.28 |  | 23.1% | 100% | 76.9%
XGL | 878 | 12 | 0 | 155 | 265 | 1 | 0 | 133 | 1266.88 | 13.12 | 0 | 1641.6 | 22.83% | 361.6 |  | 21.07% | 100% | 78.93%
XGR | 930 | 0 | 10 | 104 | 210 | 0 | 2 | 303 | 1228.8 | 0 | 12.8 | 1826.24 | 32.71% | 584.64 |  | 56.6% | 100% | 43.4%
XOM | 1298 | 11 | 0 | 106 | 179 | 0 | 0 | 357 | 1532.48 | 10.56 | 0 | 2216 | 30.84% | 672.96 |  | 60.31% | 100% | 39.69%
CORE Sites
Site Name | [8 empty] | Used (m²) | Reserved (m²) | Forecast (m²) | Total usable space (based on cab positions and front/back space) | % usable space remaining | Remaining (m²) |  | % usable space remaining
XAN | 847 | 0 | 2 | 94 | 136 | 0 | 0 | 190 | 1030.72 | 0 | 1.92 | 1426.88 | 27.76% | 394.24 |  | 44.65% | 100% | 55.35%
XCY | 990 | 0 | 0 | 83 | 167 |  | 0 | 444 | 1217.6 | 0 | 0 | 2007.68 | 39.35% | 790.08 |  | 64.1% | 100% | 35.9%
XER | 669 | 0 | 0 | 32 | 183 | 0 | 0 | 201 | 935.04 | 0 | 0 | 1287.36 | 27.37% | 352.32 |  | 50.46% | 100% | 49.54%
XKS | 1754 | 6 | 0 | 108 | 301 | 0 | 0 | 514 | 2165.44 | 5.76 | 0 | 3091.52 | 29.96% | 920.32 |  | 57.82% | 100% | 42.18%
XKS (1st) | 580 |  | 0 | 39 | 131 |  | 0 | 171 | 766.4 | 0 | 0 | 1077.44 | 28.87% | 311.04 |  | 55.22% | 100% | 44.78%
XKS (2nd) | 582 | 0 | 0 | 39 | 125 |  | 0 | 148 | 758.72 | 0 | 0 | 1032.96 | 26.55% | 274.24 |  | 40.73% | 100% | 59.27%
XKS (3rd) | 592 |  | 0 | 30 | 45 | 0 | 0 | 195 | 640.32 | 0 | 0 | 981.12 | 34.74% | 340.8 |  | 81.03% | 100% | 18.97%
XRM | 1015 | 0 | 2 | 61 | 216 | 0 | 2 | 377 | 1320 | 0 | 5.12 | 1986.88 | 33.56% | 661.76 |  | 58.98% | 100% | 41.02%
XSN | 1161 | 0 | 14 | 43 | 145 | 0 | 0 | 521 | 1346.56 | 0 | 13.44 | 2234.88 | 39.75% | 874.88 |  | 70.14% | 100% | 29.86%
XSY | 818 | 0 | 0 | 43 | 186 | 0 | 0 | 283 | 1082.88 | 0 | 0 | 1576.96 | 31.33% | 494.08 |  | 56.84% | 100% | 43.16%
[17 empty] | 89.06% |  | 110.9%
| Current Usage (S) | Forecast Cab Deployment (S) | Remaining Capacity (S) | Current Usage (D) | Forecast Cab Deployment (D) | Remaining Capacity (D) | [10 empty] | 0.86119 |  | 1.1388
Pie Chart | 15950 | 38 | 1612 | 3255 | 18 | 4614 | [10 empty] | 0.85995 |  | 1.1401
[17 empty] | 0.80919 |  | 1.1908
[17 empty] | 0.76289 |  | 1.2371
[17 empty] | 0.97326 |  | 1.0267
Site Name Non-Core | Total Eqpt Rm Area (m²) | Total Footprints (S) | Total Footprints (D)-after calc | Standard Cab Footprints Spare | Deep Cab Footprints Spare-after calc |  | Calc- Deep Cabs Tiles | Deep Cabs Footprints | [8 empty] | 1.4135 |  | 0.58653
XBL | 373 | 207 | 13 | 104 | 9 |  | 12 | 9 | [8 empty] | #N/A |  | #N/A
XCE | 1046 | 643 | 52 | 527 | 46 |  | 62 | 46 | [8 empty] | #N/A |  | #N/A
XCF | 666 | 391 | 12 | 269 | 12 |  | 16 | 12 | [8 empty] | #N/A |  | #N/A
XCN | 995 | 630 | 6 | 450 | 5 |  | 7 | 5
TGW | 67 | 29 | 0 | 8 | 0 |  |  | 0
XLR | 694 | 396 | 0 | 171 | 0 |  |  | 0
XNE (XNE001) | 588 | 336 | 0 | 252 | 0
XNE (XNE002) | 108 | 172 | 7 | 99 | 7 |  | 10 | 7
XNY | 966 | 512 | 21 | 265 | 7 |  | 10 | 7
XNY COMP RM | 166 | 55 | 0 | 4 | 0
XOD (Grd Flr) | 250 | 156 | 0 | 56 | 0 |  |  | 0
XOD (1st Flr) | 252 | 156 | 0 | 115 | 0
XSD | 939 | 640 | 9 | 488 | 1 |  | 2 | 1
TWN | 268 | 105 | 0 | 41 | 0 |  |  | 0
Graphing Calculations Non-Core
Site Name | Current Usage (S) | Reserved no of cabs (S) | Forecast no of cabs (S) | Remaining Capacity (S) | Current Usage (D) | Reserved no of cabs (D) | Forecast no of cabs (D) | Remaining Capacity (D) |  | Used (m²) | Reserved (m²) | Forecast (m²) | Total usable space (based on cab positions and front/back space) | % usable space remaining | Remaining (m²)
XBL | 103 |  | 0 | 104 | 4 |  | 0 | 9 |  | 105.28 | 0 | 0 | 219.52 | 52.04% | 114.24
XCE | 116 |  | 0 | 527 | 6 |  | 0 | 46 |  | 120.96 | 0 | 0 | 700.48 | 82.73% | 579.52
XCF | 122 |  | 1 | 268 | 0 |  | 0 | 12 |  | 117.12 | 0 | 0.96 | 394.56 | 70.32% | 276.48
XCN | 180 |  | 0 | 450 | 1 |  | 0 | 5 |  | 174.4 | 0 | 0 | 614.4 | 71.61% | 440
TGW | 21 |  | 0 | 8 | 0 |  | 0 | 0 |  | 20.16 | 0 | 0 | 27.84 | 27.59% | 7.68
XLR | 225 |  | 10 | 161 | 0 |  | 0 | 0 |  | 216 | 0 | 9.6 | 380.16 | 43.18% | 154.56
XNE (XNE001) | 84 |  | 0 | 252 | 0 |  | 0 | 0 |  | 80.64 | 0 | 0 | 322.56 | 75% | 241.92
XNE (XNE002) | 73 |  | 0 | 99 | 0 |  | 1 | 6 |  | 70.08 | 0 | 1.6 | 176.32 | 60.25% | 104.64
XNY | 247 |  | 1 | 264 | 14 |  | 0 | 7 |  | 259.52 | 0 | 0.96 | 525.12 | 50.58% | 264.64
XNY COMP RM | 51 |  | 4 | 0 | 0 |  | 0 | 0 |  | 48.96 | 0 | 3.84 | 52.8 | 7.273% | 0
XOD (Grd Flr) | 100 |  | 0 | 56 | 0 |  | 0 | 0 |  | 96 | 0 | 0 | 149.76 | 35.9% | 53.76
XOD (1st Flr) | 41 |  | 0 | 115 | 0 |  | 0 | 0 |  | 39.36 | 0 | 0 | 149.76 | 73.72% | 110.4
XSD | 152 |  | 0 | 488 | 8 |  | 1 | 0 |  | 158.72 | 0 | 1.6 | 628.8 | 74.76% | 468.48
TWN | 64 |  | 0 | 41 | 0 |  | 0 | 0 |  | 61.44 | 0 | 0 | 100.8 | 39.05% | 39.36
| Current Usage | Forecast Cab Deployment | Remaining Capacity
XNY COMP RM | 51 | 0 | 4
| Used (m²) | Forecast (m²) | Remaining (m²)
m² | 48.96 | 0 | 3.84
| Current Usage (S) | Forecast Cab Deployment (S) | Remaining Capacity (S) | Current Usage (D) | Forecast Cab Deployment (D) | Remaining Capacity (D)
Pie Chart | 1579 | 2833 | 33 | 0 | 2 | 85
XKS Breakdown | Suite Lines Spare | Spare Capacity (m²) | Forecast Cab Deployment | Known Forecast (m²) | Suite Lines In Site | Deployed Capacity (m²) | Max Useable Capacity (m²)
Basement | 20 | 170 | 1 | 0.8 | 23 | 195.5
First Floor | 14 | 119 | 6 | 4.8 | 27 | 229.5
Second Floor | 8.5 | 72.25 | 3 | 2.4 | 27 | 229.5
Third Floor | 16.5 | 140.25 | 28 | 22.4 | 27 | 229.5
Graphing Calc | Current Usage (m²) | Known Forecast (m²) | Available Capacity (m²) | Max Useable Capacity (m²) |  |  | Quarter of total deployed Capacity(m2) |  |  | Left to hit quarter (m2)
Basement | 25.5 | 0.8 | 169.2 |  |  |  | 48.875 |  |  | 120.325
First Floor | 110.5 | 4.8 | 114.2 |  |  |  | 57.375 |  |  | 56.825
Second Floor | 157.25 | 2.4 | 69.85 |  |  |  | 57.375 |  |  | 12.475
Third Floor | 89.25 | 22.4 | 117.85 |  |  |  | 57.375 |  |  | 60.475
XOM Graph Calcs | Current Usage (m²) | Known Forecast (m²) | Available Capacity (m²)
East | 169.5 | 3.2 | 382
West | 127.5 | 1.6 | 221
Total | 1298 | 0 | 603
Graphing Calcs Non Strat CORE
Site Name | Used (m²) | Forecast (m²) | Remaining (m²)
XER | 935.04 | 0 | 352.32
XEH | 1058.24 | 3.84 | 273.28
XKS | 2165.44 | 0 | 920.32
XSN | 1346.56 | 13.44 | 874.88
XSY | 1082.88 | 0 | 494.08
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is the TOTAL area, NOT usable area
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inc HAC
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inc HAC
Note on B5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Vax Rm= 9m²
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2= 450m²
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2= 598m²
Note on J21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: allowing for front/back space
Note on J32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: allowing for front/back space
Note on M36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Basement figs omitted
Note on B49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is the TOTAL area, NOT usable area
Note on B50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2=59m², Sw Rm 3=152m², Sw Rm 4=145m², Sw Rm 5= 18m²
Note on B51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm2= 445m²
Note on B52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Comms Rm= 22m²
Note on B53: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Comms Rm=26m²
Note on B54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2= 16m²
Note on B55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2= 181m²
Note on B56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 3= 328m²
Note on B58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm 2= 159m²
Note on B61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sw Rm B= 150m²
Note on C93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average suit line area 8.5m2
Note on E93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: number of cabs multiplied by average 0.8m2 per cab
Note on G93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Area currently ready for immediate deployment. Taken as total number of suite lines in site. Average suite line 8.5(m2)
Note on H93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Taken as max site can support if we fit-out unused areas. To be done for April report
Note on B94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F=20 H=0
Note on B95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F=10 H=8
Note on B96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F=5 H=7
Note on B97: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: F=16 H=1
Note on B98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average suit line area 8.5m2
Note on D98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Area currently ready for immediate deployment. Taken as total number of suite lines in site. Average suite line 8.5(m2)
Note on E98: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Taken as max site can support if we fit-out unused areas
Note on B105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average suit line area 8.5m2
Note on D105: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Area currently ready for immediate deployment. Taken as total number of suite lines in site. Average suite line 8.5(m2)

## Building Capability
Site Name | Current DC Usage (kW) | Deployed DC Capacity (kW) | Max Usable DC Capacity (kW) | Max Technology Load (kW) | Max Usable Technology Load (kW) | Tactical Expansion Cap |  |  |  | Demand on Building in Current limit (kW)
[10 empty] | A&B | A or B
XAN | 173.528 | 630 | 315 | 630 | 315 |  |  |  |  | 680.4 | 340.2
XBE | 372.671 | 1008 | 504 | 1008 | 504 |  |  |  |  | 1088.64 | 544.32
XCY | 126.44 | 630 | 315 | 630 | 315 |  |  |  |  | 680.4 | 340.2
XEH | 285.6345 | 756 | 378 | 756 | 378 |  |  |  |  | 680.4 | 340.2
XER | 83.0035 | 504 | 252 | 600 | 300 |  |  |  |  | 544.32 | 272.16
XGR | 260.183 | 936 | 465 | 930 | 465 |  |  |  |  | 680.4 | 340.2
XGL | 295.172 | 954 | 462 | 960 | 462 |  |  |  |  | 842.4 | 421.2
XKS | 127.4755 | 798 | 398 | 966 | 483 |  |  |  |  | 861.84 | 430.92
XLD | 331.251 | 1002 | 480 | 956 | 460 |  |  |  |  | 855.36 | 427.68
XMS | 367.766 | 978 | 480 | 960 | 481 |  |  |  |  | 952.56 | 476.28
XOM | 293.21 | 978 | 465 | 946 | 468 |  |  |  |  | 822.96 | 411.48
XRM | 100.2255 | 630 | 315 | 630 | 315 |  |  |  |  | 680.4 | 340.2
XSN | 95.3205 | 504 | 252 | 600 | 300 |  |  |  |  | 544.32 | 272.16
XSY | 111.7795 | 609 | 304 | 609 | 304.5 |  |  |  |  | 657.72 | 328.86
[6 empty] | DC Output Load Per Rect (A) |  | Effiency |  | Real Load on Building (kW) |  | Building load with Rectifiers in Current Limit 92% Efficent (kW)
Site Name | Plant Name | Type | DC Current Load (A) | Number of Rectifiers | Rectifier Capacity (kW) | A&B | A or B | A&B | A or B | A&B | A or B | A&B | A or B
Acton | PEAAN | eSure | 629 | 36 | 3.5 | 17.4722 | 34.9444 | 0.92 | 0.97 | 37.0229 | 35.3089 | 136.08 | 68.04
Acton | PEBAN | eSure | 621 | 36 | 3.5 | 17.25 | 34.5 | 0.92 | 0.97 | 36.5521 | 34.8598 | 136.08 | 68.04
Acton | PECAN | eSure | 462 | 36 | 3.5 | 12.8333 | 25.6667 | 0.92 | 0.97 | 27.1933 | 25.9344 | 136.08 | 68.04
Acton | PEFAN | eSure | 713 | 36 | 3.5 | 19.8056 | 39.6111 | 0.97 | 0.97 | 40.0243 | 40.0243 | 136.08 | 68.04
Acton | PEGAN | eSure | 759 | 36 | 3.5 | 21.0833 | 42.1667 | 0.97 | 0.97 | 42.6065 | 42.6065 | 136.08 | 68.04
Basingstoke | PEABE | eSure | 816 | 36 | 3.5 | 22.6667 | 45.3333 | 0.97 | 0.92 | 45.8062 | 48.0298 | 136.08 | 68.04
Basingstoke | PEBBE | eSure | 840 | 36 | 3.5 | 23.3333 | 46.6667 | 0.97 | 0.92 | 47.1534 | 49.4424 | 136.08 | 68.04
Basingstoke | PECBE | eSure | 809 | 36 | 3.5 | 22.4722 | 44.9444 | 0.97 | 0.92 | 45.4132 | 47.6177 | 136.08 | 68.04
Basingstoke | PEEBE | eSure | 869 | 36 | 3.5 | 24.1389 | 48.2778 | 0.97 | 0.92 | 48.7813 | 51.1493 | 136.08 | 68.04
Basingstoke | PEFBE | eSure | 847 | 36 | 3.5 | 23.5278 | 47.0556 | 0.97 | 0.92 | 47.5463 | 49.8544 | 136.08 | 68.04
Basingstoke | PEGBE | eSure | 878 | 36 | 3.5 | 24.3889 | 48.7778 | 0.97 | 0.92 | 49.2865 | 51.6791 | 136.08 | 68.04
Basingstoke | PEHBE | eSure | 872 | 36 | 3.5 | 24.2222 | 48.4444 | 0.97 | 0.92 | 48.9497 | 51.3259 | 136.08 | 68.04
Basingstoke | PEIBE | eSure | 907 | 36 | 3.5 | 25.1944 | 50.3889 | 0.97 | 0.92 | 50.9144 | 53.386 | 136.08 | 68.04
Crawley | PEACY | eSure | 391 | 36 | 3.5 | 10.8611 | 21.7222 | 0.92 | 0.97 | 23.0143 | 21.9488 | 136.08 | 68.04
Crawley | PEBCY | eSure | 497 | 36 | 3.5 | 13.8056 | 27.6111 | 0.92 | 0.97 | 29.2534 | 27.8991 | 136.08 | 68.04
Crawley | PECCY | eSure | 609 | 36 | 3.5 | 16.9167 | 33.8333 | 0.92 | 0.97 | 35.8457 | 34.1862 | 136.08 | 68.04
Crawley | PEDCY | eSure | 472 | 36 | 3.5 | 13.1111 | 26.2222 | 0.92 | 0.97 | 27.7819 | 26.4957 | 136.08 | 68.04
Crawley | PEECY | eSure | 351 | 36 | 3.5 | 9.75 | 19.5 | 0.92 | 0.97 | 20.6599 | 19.7034 | 136.08 | 68.04
Edinburgh | PECEH | eSure | 836 | 36 | 3.5 | 23.2222 | 46.4444 | 0.97 | 0.92 | 46.9289 | 49.207 | 136.08 | 68.04
Edinburgh | PEDEH | eSure | 899 | 36 | 3.5 | 24.9722 | 49.9444 | 0.97 | 0.92 | 50.4654 | 52.9151 | 136.08 | 68.04
Edinburgh | PEEEH | eSure | 865 | 36 | 3.5 | 24.0278 | 48.0556 | 0.97 | 0.92 | 48.5568 | 50.9139 | 136.08 | 68.04
Edinburgh | PEFEH | eSure | 824 | 36 | 3.5 | 22.8889 | 45.7778 | 0.97 | 0.92 | 46.2552 | 48.5006 | 136.08 | 68.04
Edinburgh | PEGEH | eSure | 944 | 36 | 3.5 | 26.2222 | 52.4444 | 0.97 | 0.92 | 52.9914 | 55.5638 | 136.08 | 68.04
Edinburgh | PEHEH | eSure | 873 | 36 | 3.5 | 24.25 | 48.5 | 0.97 | 0.92 | 49.0059 | 51.3848 | 136.08 | 68.04
Esher | PEDER | eSure | 415 | 36 | 3.5 | 11.5278 | 23.0556 | 0.92 | 0.97 | 24.4269 | 23.296 | 136.08 | 68.04
Esher | PEEER | eSure | 371 | 36 | 3.5 | 10.3056 | 20.6111 | 0.92 | 0.97 | 21.8371 | 20.8261 | 136.08 | 68.04
Esher | PEFER | eSure | 426 | 36 | 3.5 | 11.8333 | 23.6667 | 0.92 | 0.97 | 25.0744 | 23.9135 | 136.08 | 68.04
Esher | PEGER | eSure | 311 | 36 | 3.5 | 8.6389 | 17.2778 | 0.92 | 0.92 | 18.3055 | 18.3055 | 136.08 | 68.04
Gloucester | PEAGR | eSure | 641 | 36 | 3.5 | 17.8056 | 35.6111 | 0.92 | 0.97 | 37.7293 | 35.9825 | 136.08 | 68.04
Gloucester | PEBGR | eSure | 765 | 36 | 3.5 | 21.25 | 42.5 | 0.97 | 0.97 | 42.9433 | 42.9433 | 136.08 | 68.04
Gloucester | PECGR | eSure | 716 | 36 | 3.5 | 19.8889 | 39.7778 | 0.97 | 0.97 | 40.1927 | 40.1927 | 136.08 | 68.04
Gloucester | PEDGR | eSure | 711 | 36 | 3.5 | 19.75 | 39.5 | 0.97 | 0.97 | 39.912 | 39.912 | 136.08 | 68.04
Gloucester | PEEGR | eSure | 705 | 36 | 3.5 | 19.5833 | 39.1667 | 0.97 | 0.97 | 39.5752 | 39.5752 | 136.08 | 68.04
Gravelly Hill | BMGMTX-DCSYS01 | HDR48-ES | 766 | 44 | 3 | 17.4091 | 34.8182 | 0.92 | 0.92 | 45.0868 | 45.0868 | 142.56 | 71.28
Gravelly Hill | BMGMTX-DCSYS02 | HDR48-ES | 785 | 44 | 3 | 17.8409 | 35.6818 | 0.92 | 0.92 | 46.2051 | 46.2051 | 142.56 | 71.28
Gravelly Hill | PECGL | eSure | 858 | 36 | 3.5 | 23.8333 | 47.6667 | 0.97 | 0.92 | 48.1638 | 50.5019 | 136.08 | 68.04
Gravelly Hill | BMGMTX-DCSYS04 | HDR48-ES | 797 | 44 | 3 | 18.1136 | 36.2273 | 0.92 | 0.92 | 46.9114 | 46.9114 | 142.56 | 71.28
Gravelly Hill | BMGMTX-DCSYS05 | HDR48-ES | 799 | 44 | 3 | 18.1591 | 36.3182 | 0.92 | 0.92 | 47.0291 | 47.0291 | 142.56 | 71.28
Gravelly Hill | PEFGL | eSure | 844 | 36 | 3.5 | 23.4444 | 46.8889 | 0.97 | 0.92 | 47.3779 | 49.6778 | 136.08 | 68.04
Kings Cross | PEAKS | eSure | 248 | 24 | 3.5 | 10.3333 | 20.6667 | 0.92 | 0.97 | 14.5973 | 13.9215 | 90.72 | 45.36
Kings Cross | PEBKS | eSure | 352 | 30 | 3.5 | 11.7333 | 23.4667 | 0.92 | 0.97 | 20.7187 | 19.7595 | 113.4 | 56.7
Kings Cross | PEEKS | eSure | 100 | 12 | 3.5 | 8.3333 | 16.6667 | 0.92 | 0.92 | 5.886 | 5.886 | 45.36 | 22.68
Kings Cross | PEIKS | eSure | 528 | 36 | 3.5 | 14.6667 | 29.3333 | 0.92 | 0.97 | 31.0781 | 29.6393 | 136.08 | 68.04
Kings Cross | PEJKS | eSure | 229 | 36 | 3.5 | 6.3611 | 12.7222 | 0.92 | 0.92 | 13.4789 | 13.4789 | 136.08 | 68.04
Kings Cross | PEKKS | eSure | 484 | 30 | 3.5 | 16.1333 | 32.2667 | 0.92 | 0.97 | 28.4882 | 27.1693 | 113.4 | 56.7
Kings Cross | PELKS | eSure | 161 | 24 | 3.5 | 6.7083 | 13.4167 | 0.92 | 0.92 | 9.4765 | 9.4765 | 90.72 | 45.36
Kings Cross | PEMKS | eSure | 146 | 24 | 3.5 | 6.0833 | 12.1667 | 0.92 | 0.92 | 8.5936 | 8.5936 | 90.72 | 45.36
Kings Cross | PENKS | eSure | 91 | 12 | 3.5 | 7.5833 | 15.1667 | 0.92 | 0.92 | 5.3563 | 5.3563 | 45.36 | 22.68
Leyland | LLDMTX-DCSYS01 | HDR48-ES | 901 | 44 | 3 | 20.4773 | 40.9545 | 0.92 | 0.92 | 53.0329 | 53.0329 | 142.56 | 71.28
Leyland | LLDMTX-DCSYS02 | HDR48-ES | 810 | 44 | 3 | 18.4091 | 36.8182 | 0.92 | 0.92 | 47.6766 | 47.6766 | 142.56 | 71.28
Leyland | LLDMTX-DCSYS03 | HDR48-ES | 929 | 44 | 3 | 21.1136 | 42.2273 | 0.92 | 0.92 | 54.6809 | 54.6809 | 142.56 | 71.28
Leyland | LLDMTX-DCSYS04 | HDR48-ES | 859 | 44 | 3 | 19.5227 | 39.0455 | 0.92 | 0.92 | 50.5607 | 50.5607 | 142.56 | 71.28
Leyland | LLDMTX-DCSYS05 | HDR48-ES | 910 | 44 | 3 | 20.6818 | 41.3636 | 0.92 | 0.92 | 53.5626 | 53.5626 | 142.56 | 71.28
Leyland | LLDMTX-DCSYS06 | HDR48-ES | 898 | 44 | 3 | 20.4091 | 40.8182 | 0.92 | 0.92 | 52.8563 | 52.8563 | 142.56 | 71.28
Milton Keynes | PEAMS | eSure | 1046 | 42 | 3.5 | 24.9048 | 49.8095 | 0.97 | 0.92 | 58.7172 | 61.5676 | 158.76 | 79.38
Milton Keynes | PEBMS | eSure | 988 | 42 | 3.5 | 23.5238 | 47.0476 | 0.97 | 0.92 | 55.4614 | 58.1537 | 158.76 | 79.38
Milton Keynes | PECMS | eSure | 960 | 42 | 3.5 | 22.8571 | 45.7143 | 0.97 | 0.92 | 53.8896 | 56.5056 | 158.76 | 79.38
Milton Keynes | PEDMS | eSure | 1131 | 42 | 3.5 | 26.9286 | 53.8571 | 0.97 | 0.92 | 63.4887 | 66.5707 | 158.76 | 79.38
Milton Keynes | PEEMS | eSure | 1051 | 42 | 3.5 | 25.0238 | 50.0476 | 0.97 | 0.92 | 58.9979 | 61.8619 | 158.76 | 79.38
Milton Keynes | PEFMS | eSure | 1045 | 42 | 3.5 | 24.881 | 49.7619 | 0.97 | 0.92 | 58.6611 | 61.5087 | 158.76 | 79.38
Oldham | OLDMTX-DCSYS01 | HDR48-ES | 887 | 44 | 3 | 20.1591 | 40.3182 | 0.92 | 0.92 | 52.2088 | 52.2088 | 142.56 | 71.28
Oldham | OLDMTX-DCSYS02 | HDR48-ES | 818 | 44 | 3 | 18.5909 | 37.1818 | 0.92 | 0.92 | 48.1475 | 48.1475 | 142.56 | 71.28
Oldham | OLDMTX-DCSYS03 | HDR48-ES | 820 | 44 | 3 | 18.6364 | 37.2727 | 0.92 | 0.92 | 48.2652 | 48.2652 | 142.56 | 71.28
Oldham | OLDMTX-DCSYS04 | HDR48-ES | 615 | 34 | 3 | 18.0882 | 36.1765 | 0.92 | 0.92 | 36.1989 | 36.1989 | 110.16 | 55.08
Oldham | OLDMTX-DCSYS05 | HDR48-ES | 637 | 44 | 3 | 14.4773 | 28.9545 | 0.92 | 0.92 | 37.4938 | 37.4938 | 142.56 | 71.28
Oldham | OLDMTX-DCSYS06 | HDR48-ES | 652 | 44 | 3 | 14.8182 | 29.6364 | 0.92 | 0.92 | 38.3767 | 38.3767 | 142.56 | 71.28
Rotherham | PEARM | eSure | 401 | 36 | 3.5 | 11.1389 | 22.2778 | 0.92 | 0.97 | 23.6029 | 22.5101 | 136.08 | 68.04
Rotherham | PEBRM | eSure | 437 | 36 | 3.5 | 12.1389 | 24.2778 | 0.92 | 0.97 | 25.7218 | 24.531 | 136.08 | 68.04
Rotherham | PECRM | eSure | 533 | 36 | 3.5 | 14.8056 | 29.6111 | 0.92 | 0.97 | 31.3724 | 29.92 | 136.08 | 68.04
Rotherham | PEDRM | eSure | 256 | 36 | 3.5 | 7.1111 | 14.2222 | 0.92 | 0.92 | 15.0682 | 15.0682 | 136.08 | 68.04
Rotherham | PEERM | eSure | 212 | 36 | 3.5 | 5.8889 | 11.7778 | 0.92 | 0.92 | 12.4783 | 12.4783 | 136.08 | 68.04
Southampton | PEASN | eSure | 368 | 36 | 3.5 | 10.2222 | 20.4444 | 0.92 | 0.97 | 21.6605 | 20.6577 | 136.08 | 68.04
Southampton | PEBSN | eSure | 544 | 36 | 3.5 | 15.1111 | 30.2222 | 0.92 | 0.97 | 32.0198 | 30.5374 | 136.08 | 68.04
Southampton | PECSN | eSure | 491 | 36 | 3.5 | 13.6389 | 27.2778 | 0.92 | 0.97 | 28.9003 | 27.5623 | 136.08 | 68.04
Southampton | PEESN | eSure | 346 | 36 | 3.5 | 9.6111 | 19.2222 | 0.92 | 0.97 | 20.3656 | 19.4227 | 136.08 | 68.04
Swanley | PEASY | eSure | 538 | 36 | 3.5 | 14.9444 | 29.8889 | 0.92 | 0.97 | 31.6667 | 30.2006 | 136.08 | 68.04
Swanley | PEBSY | eSure | 498 | 36 | 3.5 | 13.8333 | 27.6667 | 0.92 | 0.97 | 29.3123 | 27.9552 | 136.08 | 68.04
Swanley | PECSY | eSure | 384 | 36 | 3.5 | 10.6667 | 21.3333 | 0.92 | 0.97 | 22.6022 | 21.5558 | 136.08 | 68.04
Swanley | PEDSY | eSure | 298 | 36 | 3.5 | 8.2778 | 16.5556 | 0.92 | 0.92 | 17.5403 | 17.5403 | 136.08 | 68.04
Swanley | PEESY | eSure | 333 | 30 | 3.5 | 11.1 | 22.2 | 0.92 | 0.97 | 19.6004 | 18.693 | 113.4 | 56.7
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: update to 465 from 300 after tactical upgrade
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Increased from 450 kW Dec 2021 Reply: Updated from 480 to 462 to reflect actual capacity post upgrade
Note on F11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reduced for 478kW to 460kW based on revised tactical figures
Note on F12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Increased from 407kW May 21 Reply: Updated to 481kW to 480kW
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Increased from 450 kW Dec 2021 Reply: Updated from 473 to 468 to reflect actual capacity post upgrade

## Battery Log
| Start | End | Replacement Range
Current FY | 2023-04-01 | 2024-03-30 | 2016-04-01 | 2017-03-31 |  | Current FY Expenditure |  | 0
Bugeting FY | 2024-04-01 | 2025-03-30 | 2017-04-02 | 2018-03-31 |  | Budget Requirement forecast |  | 321926
Battery life (years) | 7
Battery life (days) | 2556
[22 empty] | Current FY |  | Next FY
Site Name | Plant Name | Load (kW) | Estimated Autonomy Time @25degC | Battery Cab 1 | Battery Cab 2 | Battery Cab 3 | Battery Cab 4 | Battery Cab 5 | Battery Cab 6 | Battery Cab 7 | Battery Cab 8 | Battery Cab 9 | Battery Cab 10 | Battery Cab 11 | Battery Type | PO Number (for cells) | Total Number of Strings | Load Per String (kW) | Lookup value | Strings schedulled for replacement | Strings in Need of replacement | Battery Testing Requirement | Test Type | Battery Testing Requirement | Test Type | Site Name
Acton | PEAAN | 34.2805 | 3 hours | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 |  |  | SBS XL 170F-FT |  | 9 | 3.8089 | 11 | 0 | 0 | 9 | IR+HC | 9 | Discharge | Acton | PEAAN
Acton | PEBAN | 33.8445 | 3 hours | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 |  |  | SBS XL 170F-FT |  | 9 | 3.7605 | 11 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEBAN
Acton | PECAN | 25.179 | 5 hours | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 |  |  | SBS XL 170F-FT |  | 9 | 2.7977 | 13 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PECAN
Acton | PEFAN | 38.8585 | 3 hours | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 |  |  | SBS XL 170F-FT |  | 9 | 4.3176 | 11 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEFAN
Acton | PEGAN | 41.3655 | 2.5 hours | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 | 2020-10-01 |  |  | SBS XL 170F-FT |  | 9 | 4.5962 | 10 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEGAN
Basingstoke | PEABE | 44.472 | 2.5 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 4.9413 | 10 | 0 | 0 | 15 | New | 15 | IR+HC | Basingstoke | PEABE
Basingstoke | PEBBE | 45.78 | 2 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 5.0867 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEBBE
Basingstoke | PECBE | 44.0905 | 2.5 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 4.8989 | 10 | 0 | 0 | 15 | New | 15 | IR+HC |  | PECBE
Basingstoke | PEEBE | 47.3605 | 2 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 5.2623 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEEBE
Basingstoke | PEFBE | 46.1615 | 2 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 5.1291 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEFBE
Basingstoke | PEGBE | 47.851 | 1.5 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  |  | SBS XL 170F-FT |  | 8 | 5.9814 | 8 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEGBE
Basingstoke | PEHBE | 47.524 | 2 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 5.2804 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEHBE
Basingstoke | PEIBE | 49.4315 | 2 hours | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 | 2023-09-01 |  |  | SBS XL 170F-FT |  | 9 | 5.4924 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEIBE
Crawley | PEACY | 21.3095 | 6 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.3677 | 14 | 0 | 0 | 9 | IR+HC | 9 | Discharge | Crawley | PEACY
Crawley | PEBCY | 27.0865 | 4 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 3.0096 | 12 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEBCY
Crawley | PECCY | 33.1905 | 3 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 3.6878 | 11 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PECCY
Crawley | PEDCY | 25.724 | 5 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.8582 | 13 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEDCY
Crawley | PEECY | 19.1295 | 7 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.1255 | 15 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEECY
Edinburgh | PECEH | 45.562 | 2 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 5.0624 | 9 | 0 | 0 | 7 | Discharge | 7 | IR+HC | Edinburgh | PECEH
Edinburgh | PEDEH | 48.9955 | 2 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 5.4439 | 9 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEDEH
Edinburgh | PEEEH | 47.1425 | 2 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 5.2381 | 9 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEEEH
Edinburgh | PEFEH | 44.908 | 2.5 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 4.9898 | 10 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEFEH
Edinburgh | PEGEH | 51.448 | 2 hours | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 5.7164 | 9 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEGEH
Edinburgh | PEHEH | 47.5785 | 2 hours | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-12-01 |  |  | SBS XL 170F-FT |  | 9 | 5.2865 | 9 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEHEH
Esher | PEDER | 22.6175 | 5 hours | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 |  |  | SBS XL 170F-FT |  | 9 | 2.5131 | 13 | 0 | 0 | 7 | Discharge | 7 | IR+HC | Esher | PEDER
Esher | PEEER | 20.2195 | 6 hours | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 | 2020-01-01 |  |  | SBS XL 170F-FT |  | 9 | 2.2466 | 14 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEEER
Esher | PEFER | 23.217 | 5 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 |  |  | SBS XL 170F-FT |  | 9 | 2.5797 | 13 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEFER
Esher | PEGER | 16.9495 | 8 hours | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 | 2020-02-01 |  |  | SBS XL 170F-FT |  | 9 | 1.8833 | 16 | 0 | 0 | 7 | Discharge | 7 | IR+HC |  | PEGER
Gloucester | PEAGR | 34.9345 | 3 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 3.8816 | 11 | 0 | 0 | 13 | IR+HC | 13 | Discharge | Gloucester | PEAGR
Gloucester | PEBGR | 41.6925 | 2.5 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 4.6325 | 10 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEBGR
Gloucester | PECGR | 39.022 | 3 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 4.3358 | 11 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PECGR
Gloucester | PEDGR | 38.7495 | 3 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 |  |  | SBS XL 170F-FT |  | 9 | 4.3055 | 11 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEDGR
Gloucester | PEEGR | 38.4225 | 3 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 4.2692 | 11 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEEGR
Gloucester | GCRMTX-DCSYS06a | 34.8255 | 1.5 hours | 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01 |  |  | SBS XL 170F-FT |  | 5 | 6.9651 | 8 | 0 | 0 | [5 empty] | GCRMTX-DCSYS06a
Gloucester | GCRMTX-DCSYS06b | 32.5365 | 1.5 hours | 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01; 2022-11-01: 2022-03-01 |  |  | SBS XL 170F-FT |  | 5 | 6.5073 | 8 | 0 | 0 | [5 empty] | GCRMTX-DCSYS06b
Gravelly Hill | BMGMTX-DCSYS01 | 41.747 | 2.5 hours | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  |  | SBS XL 170F-FT |  | 9 | 4.6386 | 10 | 0 | 0 | 15 | New | 15 |  | Gravelly Hill | BMGMTX-DCSYS01
Gravelly Hill | BMGMTX-DCSYS02 | 42.7825 | 2.5 hours | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  |  | SBS XL 170F-FT |  | 9 | 4.7536 | 10 | 0 | 0 | 15 | New | 15 |  |  | BMGMTX-DCSYS02
Gravelly Hill | PECGL | 46.761 | 2 hours | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  |  | SBS XL 170F-FT |  | 9 | 5.1957 | 9 | 0 | 0 | 15 | New | 15 |  |  | PECGL
Gravelly Hill | BMGMTX-DCSYS04 | 43.4365 | 2.5 hours | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-04-01 | 2020-04-01 | 2020-04-01 | 2020-04-01 | 2020-04-01 | 2020-04-01 |  |  | SBS XL 170F-FT |  | 9 | 4.8263 | 10 | 0 | 0 | 7 | Discharge | 7 |  |  | BMGMTX-DCSYS04
Gravelly Hill | BMGMTX-DCSYS05 | 43.5455 | 2.5 hours | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 | 2023-06-01 |  |  | SBS XL 170F-FT |  | 9 | 4.8384 | 10 | 0 | 0 | 15 | New | 15 |  |  | BMGMTX-DCSYS05
Gravelly Hill | PEFGL | 45.998 | 2 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 5.1109 | 9 | 0 | 0 | 13 | IR+HC | 13 |  |  | PEFGL
Gravelly Hill | BMGMTX-DCSYS07a | 15.478 | 4 hours | 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01 |  |  | SBS XL 170F-FT |  | 5 | 3.0956 | 12 | 0 | 0 | [5 empty] | BMGMTX-DCSYS07a
Gravelly Hill | BMGMTX-DCSYS07b | 15.4235 | 4 hours | 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01; 2023-06-01: 2021-10-01 |  |  | SBS XL 170F-FT |  | 5 | 3.0847 | 12 | 0 | 0 | [5 empty] | BMGMTX-DCSYS07b
Kings Cross | PEAKS | 13.516 | 8 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 |  |  | SBS XL 170F-FT |  | 9 | 1.5018 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Kings Cross | PEAKS
Kings Cross | PEBKS | 19.184 | 7 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 |  |  | SBS XL 170F-FT |  | 9 | 2.1316 | 15 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEBKS
Kings Cross | PEEKS | 5.45 | 8 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-08-01 |  |  |  |  | SBS XL 170F-FT |  | 7 | 0.77857 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEEKS
Kings Cross | PEIKS | 28.776 | 4 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 |  |  | 6V165/6 |  | 9 | 3.1973 | 12 | 9 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEIKS
Kings Cross | PEJKS | 12.4805 | 8 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 |  |  | 6V165/6 |  | 9 | 1.3867 | 16 | 9 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEJKS
Kings Cross | PEKKS | 26.378 | 5 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 |  |  | 6V165/6 |  | 9 | 2.9309 | 13 | 9 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEKKS
Kings Cross | PELKS | 8.7745 | 8 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | [5 empty] | 6V165/6 |  | 6 | 1.4624 | 16 | 6 | 0 | 3 | Discharge | 3 | Replacement Due |  | PELKS
Kings Cross | PEMKS | 7.957 | 8 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | [5 empty] | 6V165/6 |  | 6 | 1.3262 | 16 | 6 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEMKS
Kings Cross | PENKS | 4.9595 | 8 hours | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | 2017-07-01 | [5 empty] | 6V165/6 |  | 6 | 0.82658 | 16 | 6 | 0 | 3 | Discharge | 3 | Replacement Due |  | PENKS
Leyland | LLDMTX-DCSYS01 | 49.1045 | 2 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 5.4561 | 9 | 0 | 0 | 13 |  | 13 |  | Leyland | LLDMTX-DCSYS01
Leyland | LLDMTX-DCSYS02 | 44.145 | 2.5 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 4.905 | 10 | 0 | 0 | 13 |  | 13 |  |  | LLDMTX-DCSYS02
Leyland | LLDMTX-DCSYS03 | 50.6305 | 2 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 5.6256 | 9 | 0 | 0 | 13 |  | 13 |  |  | LLDMTX-DCSYS03
Leyland | LLDMTX-DCSYS04 | 46.8155 | 2 hours | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 | 2021-07-01 |  |  | SBS XL 170F-FT |  | 9 | 5.2017 | 9 | 0 | 0 | 11 |  | 11 |  |  | LLDMTX-DCSYS04
Leyland | LLDMTX-DCSYS05 | 49.595 | 2 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 5.5106 | 9 | 0 | 0 | 13 |  | 13 |  |  | LLDMTX-DCSYS05
Leyland | LLDMTX-DCSYS06 | 48.941 | 2 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 5.4379 | 9 | 0 | 0 | 13 |  | 13 |  |  | LLDMTX-DCSYS06
Leyland | LLDMTX-DCSYS07a | 20.9825 | 3 hours | 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01 |  |  | SBS XL 170F-FT |  | 5 | 4.1965 | 11 | 0 | 0 | [5 empty] | LLDMTX-DCSYS07a
Leyland | LLDMTX-DCSYS07b | 21.037 | 3 hours | 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01; 2022-10-01: 2021-03-01 |  |  | SBS XL 170F-FT |  | 5 | 4.2074 | 11 | 0 | 0 | [5 empty] | LLDMTX-DCSYS07b
Milton Keynes | PEAMS | 57.007 | 2 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 5.7007 | 9 | 0 | 0 | 15 | New | 15 | IR+HC | Milton Keynes | PEAMS
Milton Keynes | PEBMS | 53.846 | 2 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 5.3846 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEBMS
Milton Keynes | PECMS | 52.32 | 2 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 5.232 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PECMS
Milton Keynes | PEDMS | 61.6395 | 1.5 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 6.1639 | 8 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEDMS
Milton Keynes | PEEMS | 57.2795 | 2 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 5.7279 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEEMS
Milton Keynes | PEFMS | 56.9525 | 2 hours | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 | 2023-08-01 |  | SBS XL 170F-FT |  | 10 | 5.6952 | 9 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEFMS
Milton Keynes | MKSMTX-DCSYS07a | 14.2245 | 5 hours | 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01 |  | SBS XL 170F-FT |  | 5 | 2.8449 | 13 | 0 | 0 | [5 empty] | MKSMTX-DCSYS07a
Milton Keynes | MKSMTX-DCSYS07b | 14.497 | 5 hours | 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01; 2023-08-01: 2021-03-01 |  | SBS XL 170F-FT |  | 5 | 2.8994 | 13 | 0 | 0 | [5 empty] | MKSMTX-DCSYS07b
Oldham | OLDMTX-DCSYS01 | 48.3415 | 2 hours | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 |  |  | SBS XL 170F-FT |  | 9 | 5.3713 | 9 | 0 | 0 | 7 | Discharge | 7 |  | Oldham | OLDMTX-DCSYS01
Oldham | OLDMTX-DCSYS02 | 44.581 | 2.5 hours | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 | 2020-03-01 |  |  | SBS XL 170F-FT |  | 9 | 4.9534 | 10 | 0 | 0 | 7 | Discharge | 7 |  |  | OLDMTX-DCSYS02
Oldham | OLDMTX-DCSYS03 | 44.69 | 2.5 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 4.9656 | 10 | 0 | 0 | 13 | IR+HC | 13 |  |  | OLDMTX-DCSYS03
Oldham | OLDMTX-DCSYS04 | 33.5175 | 3 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 3.7242 | 11 | 0 | 0 | 13 | IR+HC | 13 |  |  | OLDMTX-DCSYS04
Oldham | OLDMTX-DCSYS05 | 34.7165 | 3 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 3.8574 | 11 | 0 | 0 | 13 | IR+HC | 13 |  |  | OLDMTX-DCSYS05
Oldham | OLDMTX-DCSYS06 | 35.534 | 3 hours | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 | 2022-10-01 |  |  | SBS XL 170F-FT |  | 9 | 3.9482 | 11 | 0 | 0 | 13 | IR+HC | 13 |  |  | OLDMTX-DCSYS06
Oldham | OLDMTX-DCSYS07a | 26.16 | 2 hours | 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01 |  |  | SBS XL 170F-FT |  | 5 | 5.232 | 9 | 0 | 0 | [5 empty] | OLDMTX-DCSYS07a
Oldham | OLDMTX-DCSYS07b | 25.6695 | 2 hours | 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01; 2022-10-01: 2021-11-01 |  |  | SBS XL 170F-FT |  | 5 | 5.1339 | 9 | 0 | 0 | [5 empty] | OLDMTX-DCSYS07b
Rotherham | PEARM | 21.8545 | 6 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2020-03-01 | 2020-03-01 |  |  | SBS XL 170F-FT |  | 9 | 2.4283 | 14 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Rotherham | PEARM
Rotherham | PEBRM | 23.8165 | 5 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  | SBS XL 170F-FT |  | 9 | 2.6463 | 13 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEBRM
Rotherham | PECRM | 29.0485 | 4 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  | SBS XL 170F-FT |  | 9 | 3.2276 | 12 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PECRM
Rotherham | PEDRM | 13.952 | 8 hours | 2021-08-01 | 2021-08-01 | 2021-08-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  | SBS XL 170F-FT |  | 9 | 1.5502 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEDRM
Rotherham | PEERM | 11.554 | 8 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  | SBS XL 170F-FT |  | 9 | 1.2838 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEERM
Southampton | PEASN | 20.056 | 6 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.2284 | 14 | 0 | 0 | 9 | IR+HC | 9 | Discharge | Southampton | PEASN
Southampton | PEBSN | 29.648 | 4 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 3.2942 | 12 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEBSN
Southampton | PECSN | 26.7595 | 4 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.9733 | 12 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PECSN
Southampton | PEESN | 18.857 | 7 hours | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 | 2020-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.0952 | 15 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEESN
Swanley | PEASY | 29.321 | 4 hours | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 |  |  | SBS XL 170F-FT |  | 9 | 3.2579 | 12 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Swanley | PEASY
Swanley | PEBSY | 27.141 | 4 hours | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 |  |  | SBS XL 170F-FT |  | 9 | 3.0157 | 12 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEBSY
Swanley | PECSY | 20.928 | 6 hours | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 |  |  | SBS XL 170F-FT |  | 9 | 2.3253 | 14 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PECSY
Swanley | PEDSY | 16.241 | 8 hours | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 |  |  | SBS XL 170F-FT |  | 9 | 1.8046 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEDSY
Swanley | PEESY | 18.1485 | 5 hours | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 | 2022-01-01 |  |  |  |  | SBS XL 170F-FT |  | 7 | 2.5926 | 13 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEESY
Bristol | PEFBL | 25.942 | 5 hours | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 | 2021-11-01 |  |  | SBS XL 170F-FT |  | 9 | 2.8824 | 13 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Bristol | PEFBL
Bristol | PEHBL | 17.9305 | 7 hours | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 |  |  | SBS XL 170F-FT |  | 9 | 1.9923 | 15 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEHBL
Cardiff | PECCF | 19.184 | 3 hours | 2022-10-01: 2018-12-01; 2022-10-01: 2018-12-01; 2022-10-01: 2018-12-01; 2022-10-01: 2017-04-01; 2022-10-01: 2017-04-01 |  |  | 6V165/6 |  | 5 | 3.8368 | 11 | 0 | 0 | 5 | IR+HC | 5 | Discharge | Cardiff | PECCF
Cardiff | PEDCF | 8.9925 | 8 hours | 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01 |  |  | SBS XL 170F-FT |  | 5 | 1.7985 | 16 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEDCF
Cardiff | PEECF | 11.445 | 6 hours | 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01; 2022-10-01: 2022-12-01 |  |  | SBS XL 170F-FT |  | 5 | 2.289 | 14 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEECF
Carlisle | PEACE | 21.8 | 6 hours | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 |  |  | SBS XL 170F-FT |  | 9 | 2.4222 | 14 | 0 | 0 | 15 | New | 15 | IR+HC | Carlisle | PEACE
Carlisle | PEBCE | 24.198 | 5 hours | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 | 2023-07-01 |  |  | SBS XL 170F-FT |  | 9 | 2.6887 | 13 | 0 | 0 | 15 | New | 15 | IR+HC |  | PEBCE
Croydon | PEFCN | 17.0585 | 8 hours | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 |  |  | SBS XL 170F-FT |  | 9 | 1.8954 | 16 | 0 | 0 | 13 | IR+HC | 13 | Discharge | Croydon | PEFCN
Croydon | PEGCN | 21.0915 | 6 hours | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 | 2022-12-01 |  |  | SBS XL 170F-FT |  | 9 | 2.3435 | 14 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEGCN
Glasgow TXO | PEJGW | 4.7415 | 6 hours | 2022-10-01: 2021-09-01; 2022-10-01: 2021-09-01 |  |  | SBS XL 170F-FT |  | 2 | 2.3708 | 14 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Glasgow TXO | PEJGW
Glasgow TXO | PEKGW | 4.6325 | 6 hours | 2022-10-01: 2021-09-01; 2022-10-01: 2021-09-01 |  |  | SBS XL 170F-FT |  | 2 | 2.3163 | 14 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEKGW
Leicester | PEFLR | 34.117 | 3 hours | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 |  |  | SBS XL 170F-FT |  | 9 | 3.7908 | 11 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Leicester | PEFLR
Leicester | PEGLR | 28.34 | 4 hours | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 | 2022-11-01 |  |  | SBS XL 170F-FT |  | 9 | 3.1489 | 12 | 0 | 0 | 13 | IR+HC | 13 | Discharge |  | PEGLR
Newbury | PEGNY | 19.947 | 6 hours | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 |  |  | SBS XL 170F-FT |  | 9 | 2.2163 | 14 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Newbury | PEGNY
Newbury | PEHNY | 17.113 | 8 hours | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 | 2021-12-01 |  |  | SBS XL 170F-FT |  | 9 | 1.9014 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEHNY
Newcastle | PEENE | 16.677 | 8 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2020-03-01 | 2020-03-01 |  |  | SBS XL 170F-FT |  | 9 | 1.853 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC | Newcastle | PEENE
Newcastle | PEFNE | 19.5655 | 5 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  |  |  | SBS XL 170F-FT |  | 7 | 2.7951 | 13 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEFNE
Newcastle | PEGNE | 8.2295 | 8 hours | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 | 2021-09-01 |  |  |  |  | SBS XL 170F-FT |  | 7 | 1.1756 | 16 | 0 | 0 | 11 | Discharge | 11 | IR+HC |  | PEGNE
Oxford | PECOD | 12.862 | 7 hours | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | [5 empty] | SBS XL 170F-FT | 1500700866 | 6 | 2.1437 | 15 | 0 | 0 | 9 | IR+HC | 9 | Discharge | Oxford | PECOD
Oxford | PEFOD | 7.521 | 8 hours | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | 2020-09-01 | [5 empty] | SBS XL 170F-FT | 1500700866 | 6 | 1.2535 | 16 | 0 | 0 | 9 | IR+HC | 9 | Discharge |  | PEFOD
Stafford | PEESD | 21.473 | 6 hours | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 |  |  | 6V165/6 | 1500700866 | 9 | 2.3859 | 14 | 9 | 0 | 3 | Discharge | 3 | Replacement Due | Stafford | PEESD
Stafford | PEGSD | 22.7265 | 5 hours | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 | 2017-06-01 |  |  | 6V165/6 | 1500700866 | 9 | 2.5252 | 13 | 9 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEGSD
Warrington TXO | PELWN | 11.3905 | 6 hours | 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01 |  |  | 6V165/6 |  | 5 | 2.2781 | 14 | 5 | 0 | 3 | Discharge | 3 | Replacement Due | Warrington TXO | PELWN
Warrington TXO | PEMWN | 8.502 | 8 hours | 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01; 2022-10-01: 2017-06-01 |  |  | 6V165/6 |  | 5 | 1.7004 | 16 | 5 | 0 | 3 | Discharge | 3 | Replacement Due |  | PEMWN
Warrington TXO | PENWN | 19.6745 | 3 hours | 2022-10-01: 2017-07-01; 2022-10-01: 2017-07-01; 2022-10-01: 2017-07-01; 2022-10-01: 2017-07-01; 2022-10-01: 2017-07-01 |  |  | 6V165/6 | 1500547536 | 5 | 3.9349 | 11 | 5 | 0 | 3 | Discharge | 3 | Replacement Due |  | PENWN
[17 empty] | 939 | 414.3821 | 1371 | 78 | 0
IR+HC Testing
Discharge Testing
Battery Characteristics Table
Time |  | 30 mins | 35 mins | 40 mins | 45 mins | 50 mins | 55 mins | 1 hour | 1.5 hours | 2 hours | 2.5 hours | 3 hours | 4 hours | 5 hours | 6 hours | 7 hours | 8 hours
6V165/6 Power discharge (watts per cell) @ 20degC to 1.8Vper cell |  | 327 | 298 | 275 | 253 | 238.7 | 224.3 | 210 | 150 | 120 | 102 | 89.6 | 71.3 | 59.4 | 50 | 43.8 | 40.3
6V165/6 Power discharge (watts per cell) @ 25degC to 1.8Vper cell |  | 336.2 | 306.3 | 282.7 | 260.1 | 245.4 | 230.6 | 215.9 | 154.2 | 123.4 | 104.9 | 92.1 | 73.3 | 61.1 | 51.4 | 45 | 41.4
16 Block Configuration (kW) @20degC |  | 15.696 | 14.304 | 13.2 | 12.144 | 11.4576 | 10.7664 | 10.08 | 7.2 | 5.76 | 4.896 | 4.3008 | 3.4224 | 2.8512 | 2.4 | 2.1024 | 1.9344
16 Block Configuration (kW) @25degC |  | 16.1376 | 14.7024 | 13.5696 | 12.4848 | 11.7792 | 11.0688 | 10.3632 | 7.4016 | 5.9232 | 5.0352 | 4.4208 | 3.5184 | 2.9328 | 2.4672 | 2.16 | 1.9872
Max load support at 9 strings (kW) @25degC |  | 145.2384 | 132.3216 | 122.1264 | 112.3632 | 106.0128 | 99.6192 | 93.2688 | 66.6144 | 53.3088 | 45.3168 | 39.7872 | 31.6656 | 26.3952 | 22.2048 | 19.44 | 17.8848
Financial Forecast
Single Cell cost | 333
String Cost | 3114
| Current FY |  | Current FY+ 1 years | 2022-10-01: Current FY+ 2 years; 2022-10-01: Current FY+ 3 years; 2022-10-01: Current FY+ 4 years; 2022-10-01: Current FY+ 5 years | Current FY+ 6 years |  | Current FY+ 7 years
Number of strings | 0 |  | 80 | 2022-10-01: 3; 2022-10-01: 109; 2022-10-01: 170; 2022-10-01: 229 | 163 |  | 185
Estimated HW Cost | 0 |  | 298944 | 2022-10-01: 12354.795; 2022-10-01: 516224.5177; 2022-10-01: 925888.9286; 2022-10-01: 1434310.8785 | 1174068.0095 |  | 1532410.8529
Estimated Labour Cost | 0 |  | 22981.32 | 2022-10-01: 973.5192; 2022-10-01: 41693.8008; 2022-10-01: 76650.6101; 2022-10-01: 121709.3331 | 102116.9207 |  | 455388.7374
Total Estimate | 0 |  | 321926 | 2022-10-01: 13329; 2022-10-01: 557919; 2022-10-01: 1002540; 2022-10-01: 1556021 | 1276185 |  | 1987800
Support Modelling | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| 2016-04-01 | 2017-03-30 | 2017-04-01 | 2018-03-31 | 2018-04-01 | 2019-03-31 | 2019-04-01 | 2020-03-30 | 2020-04-01 | 2021-03-30 | 2021-04-01 | 2022-03-31 | 2022-04-01 | 2023-03-31 | 2023-04-01 | 2024-03-30
| Year 0 |  | Year 6 |  | Year 5 |  | Year 4 |  | Year 3 |  | Year 2 |  | Year 1 |  | Year 7
| Replacement Due |  | Discharge |  | IR+HC |  | Discharge |  | IR+HC |  | Discharge |  | IR+HC |  | New
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| 2016-04-01 | 2017-03-31 | 2017-04-01 | 2018-03-30 | 2018-04-01 | 2019-03-31 | 2019-04-01 | 2020-03-30 | 2020-04-01 | 2021-03-30 | 2021-04-01 | 2022-03-30 | 2022-04-01 | 2023-03-31 | 2023-04-01 | 2024-03-30 | 2024-04-01 | 2025-03-30
| Reaplcement work around |  | Year 0 |  | Year 6 |  | Year 5 |  | Year 4 |  | Year 3 |  | Year 2 |  | Year 1 |  | Year 7
| IR+HC |  | Replacement Due |  | Discharge |  | IR+HC |  | Discharge |  | IR+HC |  | Discharge |  | IR+HC |  | New
| Site Name | IR | Discharge | HC | IR+HC
| XAN | 2250 | 7425 | 2525 | 4775
| XBE | 3600 | 15713.28 | 4000.34 | 7600.34
| XCY | 3149.54 | 7856.64 | 2525 | 5674.54
| XEH | 2250 | 9820.8 | 2525 | 4775
| XER | 1800 | 7856.64 | 2033.22 | 3833.22
| XGR | 2250 | 9820.8 | 2525 | 4775
| XGL | 4500 | 13749.12 | 3016.78 | 7516.78
| XKS | 5579.03 | 19641.6 | 5475.68 | 11054.71
| XLD | 5400 | 14731.2 | 3016.78 | 8416.78
| XMS | 3600 | 12767.04 | 3016.78 | 6616.78
| XOM | 5400 | 14731.2 | 3016.78 | 8416.78
| XRM | 3150 | 10802.88 | 2525 | 5675
| XSN | 1800 | 7856.64 | 2033.22 | 3833.22
| XSY | 2610.48 | 9329.76 | 2525 | 5135.48
| XBL | 900 | 3928.32 | 1049.66 | 1949.66
| XCF | 1170.97 | 3928.32 | 1673.64 | 2844.61
| XCE | 4139.52 | 12767.04 | 4000.34 | 8139.86
| XCN | 900 | 3928.32 | 1049.66 | 1949.66
| TGW | 900 | 982.08 | 557.88 | 1457.88
| TLS | 900 | 982.08 | 557.88 | 1457.88
| XLR | 1800 | 3928.32 | 1049.66 | 2849.66
| XNY | 1800 | 3928.32 | 1049.66 | 2849.66
| XNE | 1800 | 4419.36 | 1541.44 | 3341.44
| XOD | 1800 | 3928.32 | 1541.44 | 3341.44
| XSD | 1800 | 3928.32 | 1049.66 | 2849.66
| TWN | 1800 | 2964.24 | 1049.66 | 2849.66
| TWY | 900 | 491.04 | 557.88 | 1457.88
Formulas:
End = [Start]+364
End = [End, row above]+365
Replacement Range = [Start]-B5
Start = [Start, row above]+366
Charging current
A discharged VRLA battery will accept a high recharge current, but for those seeking a more economical charging system a current limit of 0.08 C10 : 0.1 C3 (A) is adequate.
Note: For a completely discharged battery, 80% of the capacity is
replaced in approximately:
10 hours at 0.1 C10
6 hours at 0.3 C10
5 hours no current limit applied
For a 6V165/6 (the current standard MTX battery ) C10 is 173 (Ah) @ 20degC
The recommended power plant capacity reserved for charging is 10-30%
Recharge % rate is calculated by ((redundant rectifier capacity in amps/number of battery strings - 2 strings per cab in 6V165/6 config)/C10 Value)*100
For a standard LPF10 NetSure deployment the recharge rate using 50% of the rectifers is 33.9%
For a standard LPF 10 eSure deployment the recharge rate using 50% of the rectifiers is 37.1%
Note on P7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL 170F-FT = High Temp 6V165/6 = Standard
Note on E8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on X32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: picked up M as majority of cells are lower year 2012 (front cab is 2013)
Note on E33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on B34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4 stud SBS390
Note on E34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on I41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on E46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on I49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I67: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on E76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on I82: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on I83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only 2 strings
Note on E89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E117: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SBS XL170-FT Deployed
Note on E118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on F118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on G118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on H118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on I118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on J118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on K118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on L118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on M118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on E119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on F119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on G119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on H119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on I119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on J119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on K119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on L119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on M119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Old XHN batteries installed Jul-19
Note on B122: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4 stud Youassa battery
Note on B140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: VPC price April-14 AMD - updated Nov 15 for budget forecast FY16/17 AMD updated Oct 28 for budget forecast 18/19 AMD - updatedt for HT batts and connection kit AMD - VPC price 16/8/2021 for LRP forcasting
Note on B141: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: String price plus connection kit 16/08/2021

## Power figures
Site Name *=CHE | Current Usage (kW) | Forecast (kW) | Reserved (kW) | Forecast + Reserved (kW) | Deployed DC Capacity (kW) | Max Useable DC Capacity (kW) | Max Technology Load (kW) | Max Useable Technology Load (kW) | Tsi Current Usage (kW) | Tsi Known Forecast (kW) | Deployed Tsi Capacity (kW)
XAN | 173.528 | 1.526 | 13.8975 | 15.4235 | 630 | 315 | 630 | 315 |  |  |  | 175.054 | 55.5727 | 44.4273
XBE | 372.671 | 57.6065 | 39.022 | 96.6285 | 1008 | 504 | 1008 | 504 |  |  |  | 430.2775 | 85.3725 | 14.6275
XCY | 126.44 | 8.066 | 0 | 8.066 | 630 | 315 | 630 | 315 |  |  |  | 134.506 | 42.7003 | 57.2997
XEH | 285.6345 | 6.3765 | 50.0855 | 56.462 | 756 | 378 | 756 | 378 |  |  |  | 292.011 | 77.2516 | 22.7484
XER | 83.0035 | 0 | 0 | 0 | 504 | 252 | 600 | 300 |  |  |  | 83.0035 | 32.9379 | 67.0621
XGR | 260.183 | 31.5664 | 119.8455 | 151.4119 | 936 | 468 | 930 | 465 |  |  |  | 291.7494 | 62.3396 | 37.6604
XGL | 295.172 | 20.3884 | 67.3075 | 87.696 | 954 | 477 | 960 | 480 |  |  |  | 315.5605 | 66.1552 | 33.8448
XKS | 127.4755 | 0 | 0 | 0 | 798 | 399 | 966 | 483 |  |  |  | 127.4755 | 31.9487 | 68.0513
XLD | 331.251 | 7.085 | 55.917 | 63.002 | 1002 | 501 | 956 | 478 |  |  |  | 338.336 | 67.5321 | 32.4679
XMS | 367.766 | 46.107 | 28.7215 | 74.8285 | 978 | 483 | 960 | 480 | 12 | 0 | 60 | 413.873 | 85.688 | 14.312
XOM | 293.21 | 16.241 | 105.5665 | 121.8075 | 978 | 489 | 946 | 473 |  |  |  | 309.451 | 63.2824 | 36.7176
XRM | 100.2255 | 14.715 | 0 | 14.715 | 630 | 315 | 630 | 315 |  |  |  | 114.9405 | 36.489 | 63.511
XSN | 95.3205 | 18.748 | 0 | 18.748 | 504 | 252 | 600 | 300 |  |  |  | 114.0685 | 45.2653 | 54.7347
XSY | 111.7795 | 0 | 0 | 0 | 609 | 304.5 | 609 | 304.5 |  |  |  | 111.7795 | 36.7092 | 63.2908
Total | 3023.66 | 228.4258 | 480.363 | 708.7889 | 10917 | 5452.5 | 11181 | 5590.5
Graphing Calculations- 9 Core Sites
Site Name | Inverter Usage (kW) | DC Usage (kW) | Reserved (kW) | Forecast (kW) | Remaining Deployed Usable Capability (kW) | Power Expansion Capability (kW)
XBE | 81.75 | 290.921 | 39.022 | 57.6065 | 34.7005 | 0
XMS | 71.94 | 295.826 | 28.7215 | 46.107 | 40.4055 | 0
XLD | 49.05 | 282.201 | 55.917 | 7.085 | 106.747 | 0
XEH | 33 | 252.6345 | 50.0855 | 6.3765 | 35.9035 | 0
XGL | 47.96 | 247.212 | 67.3075 | 20.3884 | 94.132 | 0
XGR | 32.7436 | 227.4394 | 119.8455 | 31.5664 | 56.4051 | 0
XOM | 55.59 | 237.62 | 105.5665 | 16.241 | 73.9825 | 0
XAN | 30.52 | 143.008 | 13.8975 | 1.526 | 126.0485 | 0
XCY | 17.44 | 109 | 0 | 8.066 | 180.494 | 0
XER | 7.63 | 75.3735 | 0 | 0 | 168.9965 | 48
XKS 1st floor | 0 | 38.15 | 0 | 0 | 94.85 | 28
XKS 2nd floor | 41.42 | 26.2145 | 0 | 0 | 65.3655 | 28
XKS 3rd floor | 0 | 21.691 | 0 | 0 | 111.309 | 28
XRM | 8.72 | 91.5055 | 0 | 14.715 | 200.0595 | 0
XSN | 7.63 | 87.6905 | 0 | 18.748 | 137.9315 | 48
XSY | 7.63 | 104.1495 | 0 | 0 | 192.7205 | 0
|  |  |  | ` |  |  | `
Site Name | Current Usage (kW) | Forecast (kW) | Reserved (kW) | Forecast + Reserved (kW) | Deployed DC Capacity (kW) | Max Useable DC Capacity (kW) | Max Technology Load (kW) | Max Useable Technology Load (kW)
XBL | 43.8725 | 0 | 0 | 0 | 230 | 115 | 600 | 300
XCF | 39.6215 | 0 | 0 | 0 | 229 | 114.5 | 600 | 300
XCE | 45.998 | 0 | 0 | 0 | 230 | 115 | 600 | 300
XCN | 38.15 | 0 | 0 | 0 | 230 | 115 | 600 | 300
TGW | 9.374 | 0 | 0 | 0 | 62 | 31 | 62 | 31
XLR | 62.457 | 0 | 0 | 0 | 230 | 115 | 600 | 300
XNE | 44.472 | 0 | 0 | 0 | 287 | 143.5 | 600 | 300
XNY | 37.06 | 0 | 0 | 0 | 230 | 115 | 600 | 300
XOD | 20.383 | 0 | 0 | 0 | 211 | 105.5 | 600 | 300
XSD | 44.1995 | 0 | 0 | 0 | 230 | 115 | 600 | 300
TWN | 39.567 | 0 | 0 | 0 | 171 | 85.5 | 171 | 85.5
Graphing Calculations
Site Name | Inverter Usage (kW) | DC Usage (kW) | Reserved (kW) | Forecast (kW) | Remaining Capacity (kW)
XBL | 1.2535 | 42.619 | 0 | 0 | 186.1275
XCF | 0.2507 | 39.6215 | 0 | 0 | 190.1278
XCE | 1.2535 | 44.7445 | 0 | 0 | 183.002
XCN | 2.0056 | 36.1444 | 0 | 0 | 191.85
TGW | 0.5014 | 8.8726 | 0 | 0 | 52.626
XLR | 1.7549 | 60.7021 | 0 | 0 | 167.543
XNE | 1.5042 | 42.9678 | 0 | 0 | 242.528
XNY | 10.2787 | 26.7813 | 0 | 0 | 192.94
XOD | 1.2535 | 20.383 | 0 | 0 | 189.3635
XSD | 1.7549 | 42.4446 | 0 | 0 | 185.8005
TWN | 0 | 39.567 | 0 | 0 | 131.433
Kings Cross Breakdown | Inverter Usage (kW) | DC Current Usage (kW) | Reserved (kW) | DC Forecast (kW) | Deployed DC Capacity (kW) | Max Useable DC Capacity (kW) | Max Technology Load (kW)
First Floor | 13.8067 | 38.15 | 0 | 0 | 231 | 115.5 | 120
Second Floor | 13.8067 | 67.6345 | 0 | 0 | 357 | 178.5 | 120
Third Floor | 13.8067 | 21.691 | 0 | 0 | 210 | 105 | 120
Graphing Calculations - 5 Remaining Core Sites
Site Name | Inverter Usage (kW) | DC Usage (kW) | Reserved (kW) | Forecast (kW) | Power Capability (kW)
XKS | 41.42 | 127.4755 | 0 | 0 | 483
Core Strat Sites Pwr Utilisation |  | CHE Sites Pwr Utilisation |  | Non- CHE Sites Pwr Utilisation
CHE Total Technology Load | 1366.86 | Total Technology Load | 1366.86 | Total Technology Load | 953.5865
Strategic (Non- CHE) Total Technology Load | 953.5865 | Total Technology Reserved/Forecast | 372.2405 | Total Technology Reserved/Forecast | 86.0119
CHE Total Technology Reserved/Forecast | 372.2405 | Remaining Power Capability | 0 | Remaining Power Capability | 0
Strategic (Non-CHE) Total Technology Reserved/Forecast | 86.0119 | Total Technology Forecast | 131.1869 | Total Technology Forecast | 72.1144
CHE Remaining Power Capability | 0
Strategic (Non- CHE) Remaining Power Capability | 0
CHE Total Technology Forecast | 131.1869
Strategic (Non- CHE) Total Technology Forecast | 72.1144
Non Strat Core Sites Pwr Utilisation
Total Technology Load | 703.2135
Total Technology Reserved/Forecast | 474.3298
Remaining Power Capability | 1538.1981
Total Technology Forecast | 117.6274
Agg Sites Pwr Utilisation
Total Technology Load | 383.0369
Total Technology Reserved/Forecast | 0
Remaining Power Capability | 1913.3413
Total Technology Forecast | 0
TxO NetSure chart data
| Load (kW) | Forecast (kW) | Plant Size (kW) | Type | Remaining Capacity (kW)
PEFBL | 25.942 | 0 | 57.5 | NetSure | 31.558
PEHBL | 17.9305 | 0 | 57.5 | NetSure | 39.5695
PEACE | 21.8 | 0 | 57.5 | NetSure | 35.7
PEBCE | 24.198 | 0 | 57.5 | NetSure | 33.302
PECCF | 19.184 | 0 | 57.5 | NetSure | 38.316
PEDCF | 8.9925 | 0 | 28.5 | NetSure | 19.5075
PEECF | 11.445 | 0 | 28.5 | NetSure | 17.055
PEFCN | 17.0585 | 0 | 57.5 | NetSure | 40.4415
PEGCN | 21.0915 | 0 | 57.5 | NetSure | 36.4085
PEJGW | 4.7415 | 0 | 15.5 | eSure | 10.7585
PEKGW | 4.6325 | 0 | 15.5 | eSure | 10.8675
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PEFLR | 34.117 | 0 | 57.5 | NetSure | 23.383
PEGLR | 28.34 | 0 | 57.5 | NetSure | 29.16
PEGNY | 19.947 | 0 | 57.5 | NetSure | 37.553
PEHNY | 17.113 | 0 | 57.5 | NetSure | 40.387
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PEENE | 16.677 | 0 | 57.5 | NetSure | 40.823
PEFNE | 19.5655 | 0 | 57.5 | NetSure | 37.9345
PEGNE | 8.2295 | 0 | 28.5 | NetSure | 20.2705
PECOD | 12.862 | 0 | 57.5 | NetSure | 44.638
PEFOD | 7.521 | 0 | 48 | NetSure | 40.479
PEESD | 21.473 | 0 | 57.5 | NetSure | 36.027
PEGSD | 22.7265 | 0 | 57.5 | NetSure | 34.7735
PELWN | 11.3905 | 0 | 28.5 | NetSure | 17.1095
PEMWN | 8.502 | 0 | 28.5 | NetSure | 19.998
PENWN | 19.6745 | 0 | 28.5 | NetSure | 8.8255
PEFWY | #REF! | #REF! | #REF! | #REF! | #REF!
RAG chart | Red count | 0
| Amber count | 0
| Green Count | 0
CHE power plants
| Load (kW) | Reserved (kW) | Forecast (kW) | Plant Size (kW) | Type | Remaining Capacity (kW)
PEABE | 44.472 | 4.5235 | 0 | 63 | eSure | 14.0045
PEBBE | 45.78 | 3.815 | 0 | 63 | eSure | 13.405
PECBE | 44.0905 | 2.398 | 0 | 63 | eSure | 16.5115
PEEBE | 47.3605 | 4.4145 | 0 | 63 | eSure | 11.225
PEFBE | 46.1615 | 4.905 | 0 | 63 | eSure | 11.9335
PEGBE | 47.851 | 6.54 | 0 | 63 | eSure | 8.609
PEHBE | 47.524 | 6.9215 | 0 | 63 | eSure | 8.5545
PEIBE | 49.4315 | 5.5045 | 0 | 63 | eSure | 8.064
BMGMTX-DCSYS01 | 41.747 | 1.09 | 0 | 66 | HDR48-ES | 23.163
BMGMTX-DCSYS02 | 42.7825 | 3.052 | 0 | 66 | HDR48-ES | 20.1655
PECGL | 46.761 | 8.2295 | 0 | 63 | eSure | 8.0095
BMGMTX-DCSYS04 | 43.4365 | 8.6655 | 0 | 66 | HDR48-ES | 13.898
BMGMTX-DCSYS05 | 43.5455 | 5.668 | 0 | 66 | HDR48-ES | 16.7865
PEFGL | 45.998 | 10.1915 | 0 | 63 | eSure | 6.8105
LLDMTX-DCSYS01 | 49.1045 | 3.597 | 0 | 66 | HDR48-ES | 13.2985
LLDMTX-DCSYS02 | 44.145 | 5.341 | 0 | 66 | HDR48-ES | 16.514
LLDMTX-DCSYS03 | 50.6305 | 4.6325 | 0 | 66 | HDR48-ES | 10.737
LLDMTX-DCSYS04 | 46.8155 | 3.597 | 0 | 66 | HDR48-ES | 15.5875
LLDMTX-DCSYS05 | 49.595 | 4.3055 | 0 | 66 | HDR48-ES | 12.0995
LLDMTX-DCSYS06 | 48.941 | 3.7605 | 0 | 66 | HDR48-ES | 13.2985
PEAMS | 57.007 | 3.2155 | 0 | 73.5 | eSure | 13.2775
PEBMS | 53.846 | 3.6515 | 0 | 73.5 | eSure | 16.0025
PECMS | 52.32 | 4.6325 | 0 | 73.5 | eSure | 16.5475
PEDMS | 61.6395 | 4.9595 | 0 | 73.5 | eSure | 6.901
PEEMS | 57.2795 | 2.507 | 0 | 73.5 | eSure | 13.7135
PEFMS | 56.9525 | 3.2155 | 0 | 73.5 | eSure | 13.332
Non CHE Strategic Power Plants
| Load (kW) | Reserved (kW) | Forecast (kW) | Plant Size (kW) | Type | Remaining Capacity (kW)
PEAAN | 34.2805 | 2.943 | 0 | 63 | eSure | 28.7195
PEBAN | 33.8445 | 2.943 | 0 | 63 | eSure | 29.1555
PECAN | 25.179 | 2.616 | 0 | 63 | eSure | 37.821
PEFAN | 38.8585 | 2.725 | 0 | 63 | eSure | 24.1415
PEGAN | 41.3655 | 2.6705 | 0 | 63 | eSure | 21.6345
PEACY | 21.3095 | 0 | 0 | 63 | eSure | 41.6905
PEBCY | 27.0865 | 0 | 0 | 63 | eSure | 35.9135
PECCY | 33.1905 | 0 | 0 | 63 | eSure | 29.8095
PEDCY | 25.724 | 0 | 0 | 63 | eSure | 37.276
PEECY | 19.1295 | 0 | 0 | 63 | eSure | 43.8705
PEAGR | 34.9345 | 9.701 | 0 | 63 | eSure | 28.0655
PEBGR | 41.6925 | 9.701 | 0 | 63 | eSure | 21.3075
PECGR | 39.022 | 12.9165 | 0 | 63 | eSure | 23.978
PEDGR | 38.7495 | 13.4615 | 0 | 63 | eSure | 24.2505
PEEGR | 38.4225 | 11.9355 | 0 | 63 | eSure | 24.5775
OLDMTX-DCSYS01 | 48.3415 | 8.7745 | 0 | 66 | HDR48-ES | 17.6585
OLDMTX-DCSYS02 | 44.581 | 11.663 | 0 | 66 | HDR48-ES | 21.419
OLDMTX-DCSYS03 | 44.69 | 5.6135 | 0 | 66 | HDR48-ES | 21.31
OLDMTX-DCSYS04 | 33.5175 | 10.791 | 0 | 51 | HDR48-ES | 17.4825
OLDMTX-DCSYS05 | 34.7165 | 8.611 | 0 | 66 | HDR48-ES | 31.2835
OLDMTX-DCSYS06 | 35.534 | 12.426 | 0 | 66 | HDR48-ES | 30.466
PEARM | 21.8545 | 0 | 0 | 63 | eSure | 41.1455
PEBRM | 23.8165 | 0 | 0 | 63 | eSure | 39.1835
PECRM | 29.0485 | 0 | 0 | 63 | eSure | 33.9515
PEDRM | 13.952 | 0 | 0 | 63 | eSure | 49.048
PEERM | 11.554 | 0 | 0 | 63 | eSure | 51.446
Remaining Type A sites
| Load (kW) | Reserved (kW) | Forecast (kW) | Plant Size (kW) | Type | Remaining Capacity (kW)
PECEH | 45.562 | 10.5185 | 0 | 63 | eSure | 17.438
PEDEH | 48.9955 | 10.3005 | 0 | 63 | eSure | 14.0045
PEEEH | 47.1425 | 10.0825 | 0 | 63 | eSure | 15.8575
PEFEH | 44.908 | 8.8835 | 0 | 63 | eSure | 18.092
PEGEH | 51.448 | 10.3005 | 0 | 63 | eSure | 11.552
PEDER | 22.6175 | 0 | 0 | 63 | eSure | 40.3825
PEEER | 20.2195 | 0 | 0 | 63 | eSure | 42.7805
PEFER | 23.217 | 0 | 0 | 63 | eSure | 39.783
PEGER | 16.9495 | 0 | 0 | 63 | eSure | 46.0505
PEAKS | 13.516 | 0 | 0 | 42 | eSure | 28.484
PEBKS | 19.184 | 0 | 0 | 52.5 | eSure | 33.316
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
PEEKS | 5.45 | 0 | 0 | 21 | eSure | 15.55
PEIKS | 28.776 | 0 | 0 | 63 | eSure | 34.224
PEJKS | 12.4805 | 0 | 0 | 63 | eSure | 50.5195
PEKKS | 26.378 | 0 | 0 | 52.5 | eSure | 26.122
PELKS | 8.7745 | 0 | 0 | 42 | eSure | 33.2255
PEMKS | 7.957 | 0 | 0 | 42 | eSure | 34.043
PENKS | 4.9595 | 0 | 0 | 21 | eSure | 16.0405
PEASN | 20.056 | 0 | 0 | 63 | eSure | 42.944
PEBSN | 29.648 | 0 | 0 | 63 | eSure | 33.352
PECSN | 26.7595 | 0 | 0 | 63 | eSure | 36.2405
PEESN | 18.857 | 0 | 0 | 63 | eSure | 44.143
PEASY | 29.321 | 0 | 0 | 63 | eSure | 33.679
PEBSY | 27.141 | 0 | 0 | 63 | eSure | 35.859
PECSY | 20.928 | 0 | 0 | 63 | eSure | 42.072
PEDSY | 16.241 | 0 | 0 | 63 | eSure | 46.759
PEESY | 18.1485 | 0 | 0 | 52.5 | eSure | 34.3515
| Inverter DC Usage (kW) | DC Current Usage (kW) | DC Known Forecast (kW) | Remaining Capacity (kW)
PEAOM | 18.53 | 40.657 | 10.137 | 6.7035
PEBOM | 18.53 | 34.88 | 7.957 | 14.6605
PECOM | 18.53 | 43.1095 | 4.905 | 9.483
PEFOM | 18.53 | 33.6265 | 0 | 23.871
PEGOM | 18.53 | 37.605 | 0 | 19.8925
PEHOM | 18.53 | 34.553 | 0 | 22.9445

## Floorspace Calc (hidden)
x8 Core Sites
Site Name |  | Current Usage | Forecast Cab Deployment | Remaining Capacity
XAN | Std | 847 | 2 | 94
| Deep | 136 | 0 | 190
XBE | Std | 1353 | 0 | 261
| Deep | 259 | 8 | 318
XCY | Std | 990 | 0 | 83
| Deep | 167 | 0 | 444 | Calc- Deep Cabs Tiles | Deep Cabs Footprints
XGR | Std | 930 | 10 | 104 | 26 | 19.5
| Deep | 210 | 2 | 303 | 11 | 8.25
XGL | Std | 878 | 0 | 155
| Deep | 265 | 0 | 133
XLD | Std | 922 | 0 | 111
| Deep | 282 | 0 | 168
XMS | Std | 837 | 6 | 200
| Deep | 198 | 6 | 182
XOM | Std | 1298 | 0 | 106
| Deep | 179 | 0 | 357
XRM | Std | 1015 | 2 | 61
| Deep | 216 | 2 | 377 | Hot Air Containment (do not use- Feb 21 now added to overall site figs)
[5 empty] | Site Name | Current Cab Usage | Reserved Cab Deployment | Forecast Cab Deployment | Remaining Cab Capacity | Total (m²) | Reserved (m²) | Forecast (m²) | Used (m²) | Remaining (m²)
x6 Core Sites |  |  |  |  | XBE | 48 | 1 | 2 | 9 | 96 | 1.6 | 3.2 | 76.8 | 14.4
Site Name |  | Current Usage | Forecast Cab Deployment | Remaining Capacity | XMS | 58 | 0 | 1 | 0 | 94.4 | 0 | 1.6 | 92.8 | 0
XEH | Std | 724 | 4 | 103 | XLD | 51 | 0 | 0 | 0 | 81.6 | 0 | 0 | 81.6 | 0
| Deep | 227 | 0 | 109 | XEH | 56 | 0 | 3 | 3 | 99.2 | 0 | 4.8 | 89.6 | 4.8
XER | Std | 669 | 0 | 32 | XGL | 20 | 0 | 6 | 13 | 62.4 | 0 | 9.6 | 32 | 20.8
| Deep | 183 | 0 | 201 | XAN | 8 | 0 | 4 | 5 | 27.2 | 0 | 6.4 | 12.8 | 8
XKS (1st) | Std | 580 | 0 | 39 | XGR | 7 | 2 | 0 | 12 | 33.6 | 3.2 | 0 | 11.2 | 19.2
| Deep | 131 | 0 | 171
XKS (2nd) | Std | 582 | 0 | 39
| Deep | 125 | 0 | 148
XKS (3rd) | Std | 592 | 0 | 30
| Deep | 45 | 0 | 195
XSN | Std | 1161 | 14 | 43
| Deep | 145 | 0 | 521
XSY | Std | 818 | 0 | 43
| Deep | 186 | 0 | 283
Pie Chart (S) | Non CHE Current Usage | CHE Current Usage | Forecast Cab Deployment | Remaining Capacity
| #REF! | 3990 | #REF! | #REF!
Pie Chart (D) | Non CHE Current Usage | CHE Current Usage | Forecast Cab Deployment | Remaining Capacity
| #REF! | 1004 | #REF! | #REF!
Site Name |  | Current Usage | Forecast Cab Deployment | Remaining Capacity
XBL | Std | 103 | 104 | 4
| Deep | 0 | 0 | 9
XCE | Std | 116 | 527 | 6
| Deep | 0 | 0 | 46
XCF | Std | 122 | 268 | 0
| Deep | 0 | 0 | 12
XCN | Std | 180 | 450 | 1
| Deep | 0 | 0 | 5
TGW | Std | 21 | 8 | 0
| Deep | 0 | 0 | 0
XLR | Std | 225 | 161 | 0
| Deep | 0 | 0 | 0
XNE | Std | 73 | 99 | 0
| Deep | 0 | 1 | 6
XNY | Std | 247 | 264 | 14
| Deep | 0 | 0 | 7
XNY COMP RM | Std | 51 | 0 | 4
| Deep | 0 | 0 | 0
XOD | Std | 100 | 56 | 0
| Deep | 0 | 0 | 0
XSD | Std | 152 | 488 | 8
| Deep | 0 | 1 | 0
TWN | Std | 64 | 41 | 0
| Deep | 0 | 0 | 0
Pie Chart (S) | Current Usage | Forecast Cab Deployment | Remaining Capacity
| #REF! | #REF! | #REF!
Pie Chart (D) | Current Usage | Forecast Cab Deployment | Remaining Capacity
| #REF! | 3 | #REF!
Property Technical Census viiew
|  | w | d
Std m2 | 1.152 | 600 | 800 | 600(w) x 800(d) cab + 400 front and back clearance + proportion of side corridors (worked out as 5% of both corridors at 1.2m wide)
Deep m2 | 2.208 | 800 | 1200 | 800(w) x 1200(d) cab + 600 front and back clearance + proportion of side corridors (worked out as 5% of both corridors at 1.2m wide)
Used m2 (zone C)
XAN | 1276.032
XBE | 2130.528
XCY | 1509.216
XEH | 1335.264
XER | 1174.752
XGR | 1535.04
XGL | 1596.576
XKS | #REF!
XLD | 1684.8
XMS | 1401.408
XOM | 1890.528
XRM | 1646.208
XSN | 1657.632
XSY | 1353.024
XBL | 118.656
XCE | 133.632
XCF | 140.544
XCN | 207.36
TGW | 38.016 | (manual figure)
TLS | 33.408 | (manual figure)
XLR | 259.2
XNE | 205.056 | (includes cabs in room 1)
XNY | 333.504
XOD | 172.896 | (includes 1st floor)
XSD | 175.104
TWN | 73.728
Note on H24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x10 MiO cabs are 600 wide, so calculated space as x8 800mm cabs
Note on H26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: x11 MiO cabs are 600 wide
Note on B108: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 12 cabs used, space inc for x15= 50% either side of suite line

## Graphs
NFV Sites Power Breakdown (Power exp cap- Deployed Usable Capability)
Hot Aisle Containment- discontinued Feb 21
Core sites power breakdown (Power exp cap- Deployed Usable Capability)
CORE Sites Power Breakdown
m²

## 12 Monthly Graph
|  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
XBE | 2023-02-01 | 383.68 | 120.32
| 2023-03-01 | 376.9765 | 127.0235
| 2023-04-01 | 377.2905 | 126.7095
| 2023-05-01 | 376.9765 | 127.0235
| 2023-06-01 | 378.2453 | 125.7547
| 2023-07-01 | 376.9326 | 127.0674
| 2023-08-01 | 376.5405 | 127.4595
| 2023-09-01 | 376.3225 | 127.6775
| 2023-10-01 | 376.7585 | 127.2415
| 2023-11-01 | 376.9765 | 127.0235
| 2023-12-01 | 376.6495 | 127.3505
| 2024-01-01 | 378.9127 | 125.0873
| 2024-02-01 | 372.671 | 131.329 | [14 empty] | XAN | 315
XMS |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
| 2023-02-01 | 382.9815 | 97.0185 | [14 empty] | XBE* | 504
| 2023-03-01 | 385.2705 | 94.7295 | [14 empty] | XEH** | 315
| 2023-04-01 | 384.9831 | 95.0169 | [14 empty] | XGL | 450
| 2023-05-01 | 384.6165 | 95.3835 | [14 empty] | XLD** | 450
| 2023-06-01 | 385.5796 | 94.4204 | [14 empty] | XMS* | 450
| 2023-07-01 | 390.3287 | 89.6713
| 2023-08-01 | 389.6305 | 90.3695
| 2023-09-01 | 385.434 | 94.566
| 2023-10-01 | 381.183 | 98.817
| 2023-11-01 | 377.8585 | 102.1415
| 2023-12-01 | 379.439 | 100.561
| 2024-01-01 | 380.2798 | 99.7202
| 2024-02-01 | 379.766 | 100.234
XLD |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
| 2023-02-01 | 345.094 | 134.906
| 2023-03-01 | 343.6225 | 136.3775
| 2023-04-01 | 345.966 | 134.034
| 2023-05-01 | 347.3285 | 132.6715
| 2023-06-01 | 346.2385 | 133.7615
| 2023-07-01 | 342.6415 | 137.3585
| 2023-08-01 | 344.6035 | 135.3965
| 2023-09-01 | 340.843 | 139.157
| 2023-10-01 | 327.5995 | 152.4005
| 2023-11-01 | 330.815 | 149.185
| 2023-12-01 | 330.706 | 149.294
| 2024-01-01 | 331.5235 | 148.4765
| 2024-02-01 | 331.251 | 148.749
XEH |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
| 2023-02-01 | 296.916 | 81.084
| 2023-03-01 | 295.5535 | 82.4465
| 2023-04-01 | 295.352 | 82.648
| 2023-05-01 | 295.9895 | 82.0105
| 2023-06-01 | 295.0973 | 82.9027
| 2023-07-01 | 297.4251 | 80.5749
| 2023-08-01 | 296.9705 | 81.0295
| 2023-09-01 | 294.191 | 83.809
| 2023-10-01 | 293.2645 | 84.7355
| 2023-11-01 | 292.992 | 85.008
| 2023-12-01 | 287.1605 | 90.8395
| 2024-01-01 | 286.9893 | 91.0107
| 2024-02-01 | 285.6345 | 92.3655
XGL |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
| 2023-02-01 | 295.3355 | 166.6645
| 2023-03-01 | 296.8615 | 165.1385
| 2023-04-01 | 294.26 | 167.74
| 2023-05-01 | 297.5155 | 164.4845
| 2023-06-01 | 291.8599 | 170.1401
| 2023-07-01 | 292.6604 | 169.3396
| 2023-08-01 | 293.973 | 168.027
| 2023-09-01 | 295.172 | 166.828
| 2023-10-01 | 292.556 | 169.444
| 2023-11-01 | 293.537 | 168.463
| 2023-12-01 | 289.504 | 172.496
| 2024-01-01 | 290.376 | 171.624
| 2024-02-01 | 295.172 | 166.828
XGR |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW)
| 2023-02-01 | 208.844 | 256.156
| 2023-03-01 | 215.7655 | 249.2345
| 2023-04-01 | 280.1669 | 184.8331
| 2023-05-01 | 283.9995 | 181.0005
| 2023-06-01 | 287.1369 | 177.8631
| 2023-07-01 | 287.3785 | 177.6215
| 2023-08-01 | 284.054 | 180.946
| 2023-09-01 | 263.7255 | 201.2745 |  | Site | 2017-01-01 | 2017-04-01 | 2017-07-01 | 2017-10-01 | 2018-01-01 | 2018-04-01 | 2018-07-01 | 2018-10-01 | 2019-01-01 | 2019-04-01 | 2019-07-01 | 2019-10-01 | 2020-01-01 | 2020-04-01 | 2020-07-01 | 2020-10-01 | 2021-01-01 | 2021-04-01 | 2021-07-01 | 2021-10-01 | 2022-01-01 | 2022-04-01 | 2022-07-01 | 2022-10-01 | 2023-01-01
| 2023-10-01 | 262.908 | 202.092 |  | XAN | 175.8715 | 164.2085 | 166.77 | 171.457 | 172.329 | 165.244 | 167.2605 | 168.187 | 172.874 | 179.087 | 180.286 | 182.684 | 188.2975 | 190 | 200 | 200 | 198
| 2023-11-01 | 260.7825 | 204.2175 |  | XBE | 294.409 | 299.2595 | 285.7435 | 286.452 | 305.2545 | 321.114 | 329.7795 | 330.924 | 323.5665 | 350.1625 | 340.516 | 343.241 | 369.1285 | 369 | 376 | 419 | 406
| 2023-12-01 | 260.0195 | 204.9805 |  | XCY | 143.444 | 145.188 | 146.6595 | 146.7685 | 146.0055 | 140.937 | 137.558 | 140.0105 | 141.482 | 141.4275 | 137.7215 | 141.8635 | 145.624 | 146 | 146 | 147 | 150
| 2024-01-01 | 260.4823 | 204.5177 |  | XEH | 148.5125 | 148.785 | 138.1575 | 137.9395 | 137.994 | 130.909 | 128.729 | 128.838 | 196.636 | 189.3875 | 196.527 | 199.143 | 215.7655 | 207 | 239 | 246 | 246
| 2024-02-01 | 260.183 | 204.817 |  | XER | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 77 | 77 | 77 | 77
XOM |  | Actual Load (kW) | Remaining Deployed Usable Capability (kW) |  | XGR | 161.2655 | 165.0805 | 159.685 | 159.358 | 155.87 | 151.8915 | 151.946 | 152.3275 | 154.2895 | 151.7825 | 142.4085 | 143.771 | 145.4605 | 147 | 146 | 147 | 157
| 2023-02-01 | 225.848 | 240.152 |  | XGL | 294.122 | 285.767 | 273.431 | 276.829 | 279.554 | 278.6275 | 276.284 | 275.7935 | 273.777 | 278.9925 | 277.2295 | 269.436 | 268.3815 | 268 | 271 | 274 | 296
| 2023-03-01 | 230.5895 | 235.4105 |  | XKS | 209.607 | 208.19 | 201.0505 | 201.214 | 199.579 | 197.4535 | 188.243 | 187.262 | 187.262 | 188.2975 | 191.949 | 185.082 | 141.918 | 186 | 184 | 187 | 183
| 2023-04-01 | 262.9743 | 203.0257 |  | XLD | 237.3495 | 248.4155 | 238.8045 | 239.295 | 239.731 | 235.679 | 235.9705 | 233.8995 | 226.3785 | 234.736 | 283.985 | 297.6835 | 300.553 | 311 | 324 | 333 | 382
| 2023-05-01 | 282.092 | 183.908 |  | XMS | 241.871 | 244.6505 | 243.3425 | 246.122 | 270.756 | 290.2125 | 299.75 | 302.475 | 294.4635 | 335.393 | 318.6615 | 334.3575 | 340.843 | 346 | 352 | 380 | 380
| 2023-06-01 | 283.1779 | 182.8221 |  | XOM | 228.9 | 231.0255 | 220.616 | 219.853 | 225.848 | 222.3055 | 214.0215 | 211.7325 | 199.9605 | 200.233 | 203.83 | 202.7945 | 203.1215 | 208 | 204 | 205 | 208
| 2023-07-01 | 293.9623 | 172.0377 |  | XRM | 164.59 | 168.2415 | 159.249 | 152.8725 | 153.8535 | 151.183 | 153.0905 | 150.965 | 154.453 | 154.235 | 157.614 | 144.752 | 144.9155 | 146 | 143 | 142 | 143
| 2023-08-01 | 296.262 | 169.738 |  | XSN | 133.6885 | 132.5985 | 128.729 | 129.4375 | 130.255 | 126.113 | 125.7315 | 128.402 | 127.639 | 123.8785 | 126.222 | 128.8925 | 128.402 | 132 | 132 | 133 | 133
| 2023-09-01 | 289.722 | 176.278 |  | XSY | 160.993 | 163.282 | 158.595 | 158.595 | 157.0145 | 153.363 | 152.4365 | 150.202 | 152.4365 | 151.7825 | 143.335 | 143.2805 | 143.008 | 144 | 145 | 146 | 145
| 2023-10-01 | 284.49 | 181.51
| 2023-11-01 | 282.6915 | 183.3085
| 2023-12-01 | 283.727 | 182.273
| 2024-01-01 | 292.556 | 173.444
| 2024-02-01 | 293.21 | 172.79
| Month | XBE | XMS | XLD | XEH | XGL | XGR | XOM
| 2020-02-01 | 383.68 | 382.9815 | 345.094 | 296.916 | 295.3355 | 208.844 | 225.848
| 2020-03-01 | 376.9765 | 385.2705 | 343.6225 | 295.5535 | 296.8615 | 215.7655 | 230.5895
| 2020-04-01 | 377.2905 | 384.9831 | 345.966 | 295.352 | 294.26 | 280.1669 | 262.9743
| 2020-05-01 | 376.9765 | 384.6165 | 347.3285 | 295.9895 | 297.5155 | 283.9995 | 282.092
| 2020-06-01 | 378.2453 | 385.5796 | 346.2385 | 295.0973 | 291.8599 | 287.1369 | 283.1779
| 2020-07-01 | 376.9326 | 390.3287 | 342.6415 | 297.4251 | 292.6604 | 287.3785 | 293.9623
| 2020-08-01 | 376.5405 | 389.6305 | 344.6035 | 296.9705 | 293.973 | 284.054 | 296.262
| 2020-09-01 | 376.3225 | 385.434 | 340.843 | 294.191 | 295.172 | 263.7255 | 289.722
| 2020-10-01 | 376.7585 | 381.183 | 327.5995 | 293.2645 | 292.556 | 262.908 | 284.49
| 2020-11-01 | 376.9765 | 377.8585 | 330.815 | 292.992 | 293.537 | 260.7825 | 282.6915
| 2020-12-01 | 376.6495 | 379.439 | 330.706 | 287.1605 | 289.504 | 260.0195 | 283.727
| 2021-01-01 | 378.9127 | 380.2798 | 331.5235 | 286.9893 | 290.376 | 260.4823 | 292.556
| 2021-02-01 | 372.671 | 379.766 | 331.251 | 285.6345 | 295.172 | 260.183 | 293.21

## AirCon Apr 21
Region | Asset Code | Description | Location | System | Tag | Name | AR_SEQ | Refrigerant | KW | Comments
LDC | VF507642 | CRAC UNIT 1 | MTX Room | AIRCON | AHU | ACTMTX | 61854 | R410A 16KG | 80
LDC | VF507643 | CRAC UNIT 2 | MTX Room | AIRCON | AHU | ACTMTX | 61850 | R410A 16kg | 80 | Powered down 27/01/20
LDC | VF507644 | CRAC UNIT 5 | MTX Room | AIRCON | AHU | ACTMTX | 61851 | R410a 16kg | 80
LDC | VF507645 | CRAC UNIT 4 | MTX Room | AIRCON | AHU | ACTMTX | 61852 | R410a 16kg | 80
LDC | VF507646 | CRAC UNIT 3 | MTX Room | AIRCON | AHU | ACTMTX | 61855 | R410A 16KG | 80
LDC | VF-508032 | Control Room AHU 8 | Control Room | AIRCON | AHU | ACTMTX | 52922 | R410a 2.8kg | 6
LDC | VF-508033 | Control Room AHU 9 | Control Room | AIRCON | AHU | ACTMTX | 59729 | R410a 2.8kg | 6
LDC | VF522001 | CRAC UNIT 6 | MTX Room | AIRCON | AHU | ACTMTX | 61853 | R410A 16KG | 80
Mids | 21736 | CHILLER 1 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54913 | R410A - 2 x 12.5Kg | 78
Mids | 21738 | CHILLER 2 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54914 | R410A - 2 x 12.5Kg | 78
Mids | 21740 | CHILLER 3 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54915 | R410A - 2 x 12.5Kg | 78
Mids | 21742 | CHILLER 4 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54916 | R410A - 2 x 12.5Kg | 78
Mids | 21744 | CHILLER 5 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54917 | R410A - 2 x 12.5Kg | 78
Mids | 21746 | CHILLER 6 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54918 | R410A - 2 x 12.5Kg | 78
Mids | 21748 | CHILLER 7 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54919 | R410A - 2 x 12.5Kg | 78
Mids | 21750 | CHILLER 8 | EXTERNAL COMPOUND | AIRCON | CHILLER | BMGMTX | 54920 | R410A - 2 x 12.5Kg | 78
Mids | 21752 | AHU 1 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54929 | CHILLED WATER | 78
Mids | 21753 | AHU 2 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54930 | CHILLED WATER | 78
Mids | 21754 | AHU 3 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54931 | CHILLED WATER | 78
Mids | 21755 | AHU 4 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54932 | CHILLED WATER | 78
Mids | 21756 | AHU 10 | SWITCH ROOM | AIRCON | AHU | BMGMTX | 54938 | R407C - 19.5Kg | 66
Mids | 21757 | AHU 5 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54933 | CHILLED WATER | 78
Mids | 21758 | AHU 6 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54934 | CHILLED WATER | 78
Mids | 21759 | AHU 7 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54935 | CHILLED WATER | 78
Mids | 21760 | AHU 8 | SWITCH ROOM | AIRCON | FCU | BMGMTX | 54936 | CHILLED WATER | 78
Mids | 113011 | AHU 9 | SWITCH ROOM | AIRCON | AHU | BMGMTX | 54937 | R407C - 16.5Kg | 66
TVB | VF-121823 | Toilet Extract Fan | Ground floor Toilet area | AIRCON | VENT | BSGMTX | 50544 | N/A |  | ventilation
TVB | VF-1218234 | MTX Supply Fan | 1st Floor Over MTX Space | AIRCON | VENT | BSGMTX | 50542 | Unknown |  | ventilation
TVB | VF-12182345 | FM200 Extract | 1st Floor Over MTX Space | AIRCON | FCU | BSGMTX | 50547 |  |  | ventilation
TVB | VF-511501 | Emerson Free cooling Unit chiller 1 | MTX Room | AIRCON | CHILLER | BSGMTX | 51112 | R410A 12.5KG | 82.6
TVB | VF-511502 | Emerson Free cooling chiller 2 | MTX Room | AIRCON | CHILLER | BSGMTX | 51111 | R410A 12.5KG | 82.6
TVB | VF-511503 | Emerson Free cooling chiller 3 | MTX Room | AIRCON | CHILLER | BSGMTX | 51110 | R410A 12.5KG | 82.6
TVB | VF-511504 | Emerson Free Outdoor chiller 4 | MTX Room | AIRCON | CHILLER | BSGMTX | 51109 | R410A 12.5KG | 82.6
TVB | VF-511505 | Emerson Free cooling chiller 5 | MTX Room | AIRCON | CHILLER | BSGMTX | 51108 | 12.5KG R410A | 82.6
TVB | VF-511506 | Emerson Free Cooling Unit chiller 6 | MTX Room | AIRCON | CHILLER | BSGMTX | 51116 | R410A 12.5KG | 82.6
TVB | VF-511507 | Emerson Free cooling Unit chiller 7 | MTX Room | AIRCON | CHILLER | BSGMTX | 51115 | R410A 12.5KG | 82.6
TVB | VF-511508 | Emerson Free Cooling Unit chiller 8 | MTX Room | AIRCON | CHILLER | BSGMTX | 51114 | R410A 12.5KG | 82.6
TVB | VF-511509 | Emerson Free cooling Unit chiller 9 | Compound | AIRCON | CHILLER | BSGMTX | 51113 | R410A 12.5KG | 82.6
TVB | VF-511510 | Emerson Free cooling Unit chiller 10 | MTX Room | AIRCON | CHILLER | BSGMTX | 51117 | R410A 12.5KG | 82.6
TVB | VF-511511 | VRV Offices/ Kitchen | Ground floor office area | AIRCON | AHU | BSGMTX | 50848 | R407C | 28 | non-operational/beyond economical repair
TVB | VF-511512 | Air Handling Unit Multi Split | 1st Floor Disaster recovery area | AIRCON | AHU | BSGMTX | 50849 | R410A | 10
TVB | VF-511513 | Air Handling Unit Small split | 1st Floor Disaster recovery area | AIRCON | AHU | BSGMTX | 50847 | R410A | 7
TVB | VF515001 | Chiller No10 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55929 | N/A |  | indoor unit to chiller 10
TVB | VF515002 | Chiller No1 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55922 | N/A |  | indoor unit to chiller 01
TVB | VF515003 | Chiller No 2 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55921 | N/A |  | indoor unit to chiller 02
TVB | VF-515004 | Chiller No3 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 57806 | N/A |  | indoor unit to chiller 03
TVB | VF-515005 | Chiller No4 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55925 | N/A |  | indoor unit to chiller 04
TVB | VF-515006 | Chiller No5 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55926 | N/A |  | indoor unit to chiller 05
TVB | VF-515007 | Chiller No6 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55913 |  |  | indoor unit to chiller 06
TVB | VF-515008 | Chiller No7 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55927 | N/A |  | indoor unit to chiller 07
TVB | VF-515009 | Chiller No 8 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55928 | N/A |  | indoor unit to chiller 08
TVB | VF-515010 | Chiller No 9 indoor unit | MTX Room | AIRCON | FCU | BSGMTX | 55917 | N/A |  | indoor unit to chiller 09
SWW | VF 504005 | Chiller 1 | COMPOUND | AIRCON | CHILLER | BTLMTX | 51508 | R410a 18KG | 110
SWW | VF 504006 | Chiller 2 | COMPOUND | AIRCON | CHILLER | BTLMTX | 51509 | R410a 18KG | 110
SWW | VF112074 | A/C Unit | Comms Rm Switch Rm 3 | AIRCON | AHU | BTLMTX | 58775 | R410a 1.8Kg | 3
SWW | VF-111117 | Liebert Unit No 1 | Switchroom | AIRCON | AHU | CDFMTX | 50664 | R407c 27KG | 60
SWW | VF-111118 | Liebert Unit No 2 | Switchroom | AIRCON | AHU | CDFMTX | 50665 | R407c 26KG | 60
SWW | VF-111119 | Liebert Unit No 4 | Switchroom | AIRCON | AHU | CDFMTX | 50666 | R407c 25KG | 60
SWW | VF-111120 | Liebert Unit No 3 | Switchroom | AIRCON | AHU | CDFMTX | 50667 | R407c 31KG | 60
SWW | VF504008 | Air Handling Unit CU1 | Comms Room | AIRCON | AHU | CDFMTX | 55836 | R417A 3.6KG | 3
SWW | VF504011 | Air Handling Unit SECURITY OFFICE | Throughout | AIRCON | AHU | CDFMTX | 55838 | R417A 3.6KG | 2.5
SWW | VF-983854 | Air Handling Unit Small split | Comms Room | AIRCON | AHU | CDFMTX | 50737 | R410a 1.7KG | 6
LSSE | 510515 | Free cooling Unit chiller 1 | MTX Room | AIRCON | AHU | CLYMTX | 53002 | 12.5KG OF R410A | 80 | In Use
LSSE | 510516 | Free cooling Unit chiller 2 | MTX Room | AIRCON | AHU | CLYMTX | 53003 | 12.5KG OF R410A | 80 | In Use
LSSE | 510517 | Free cooling Unit chiller 3 | MTX Room | AIRCON | AHU | CLYMTX | 53004 | 12.5KG OF R410A | 80 | In Use
LSSE | 510518 | Free cooling Unit chiller 4 | MTX Room | AIRCON | AHU | CLYMTX | 53006 | 12.5KG OF R410A | 80 | In Use
LSSE | 510519 | Free cooling Unit chiller 5 | MTX Room | AIRCON | AHU | CLYMTX | 53007 | 12.5KG OF R410A | 80 | In Use
LSSE | 510520 | Free cooling Unit chiller 6 | MTX Room | AIRCON | AHU | CLYMTX | 53008 | 12.5KG OF R410A | 80 | In Use
LSSE | VF-119439 | AHU 7 | Control Room | AIRCON | AHU | CLYMTX | 53023 | 5.4KG OF R407C | 7 | In Use
LSSE | VF-119440 | AHU 8 | Control Room | AIRCON | AHU | CLYMTX | 53024 | 4KG OF R407C | 7 | In Use
NW | VF-120516 | Liebert AC 1 |  | AIRCON | AHU | CSLMTX | 51968 | R407 32KG | 60
NW | VF-120517 | Liebert AC 2 |  | AIRCON | AHU | CSLMTX | 52060 | R407 32KG | 60 | changing to Airedale 40 kw
NW | VF-120518 | Liebert AC 3 |  | AIRCON | AHU | CSLMTX | 52061 | R407 32KG | 60 | changing to Airedale 40 kw
NW | VF-120519 | Liebert AC 4 |  | AIRCON | AHU | CSLMTX | 52062 | R407 32KG | 60 | changing to Airedale 40 kw
NW | VF-120520 | Liebert AC 6 |  | AIRCON | AHU | CSLMTX | 52063 | R407 32KG | 60
NW | VF-120521 | Liebert AC 5 |  | AIRCON | AHU | CSLMTX | 52064 | R407 32KG | 60 | changing to Airedale 40 kw
NW | VF-120522 | A/C Offices & Mess Room |  | AIRCON | AHU | CSLMTX | 52105 | R407 7KG | 7
NW | VF-120541 | AHU Supply - Office |  | AIRCON | AHU | CSLMTX | 51945 | R407 7KG | 7
LSSE | 510509 | Chiller 1 | MTX ROOM | AIRCON | CHILLER | CYNMTX | 52888 | 10.5KG OF R410A | 70 | In Use
LSSE | 510510 | Chiller 2 | MTX ROOM | AIRCON | CHILLER | CYNMTX | 52889 | 10.5KG OF R410A | 70 | In Use
LSSE | 510511 | Chiller 3 | MTX ROOM | AIRCON | CHILLER | CYNMTX | 52890 | 10.5KG OF R410A | 70 | In Use
LSSE | 510512 | AHU 4 | MTX ROOM | AIRCON | AHU | CYNMTX | 52891 | 38KG OF R410A | 100 | Runs if temperature rise above a certain setpoint
LSSE | 510513 | AHU 5 | MTX ROOM | AIRCON | AHU | CYNMTX | 52892 | 31.2KG OF R410A | 100 | Runs if temperature rise above a certain setpoint
LSSE | 510514 | AHU 6 | MTX ROOM | AIRCON | AHU | CYNMTX | 52893 | 30KG OF R407C | 100 | Runs if temperature rise above a certain setpoint
LSSE | 119701 | Unit 1 | Old Plantroom | AIRCON | AHU | ESHMTX | 51884 | 20KG OF R407C | 85 | Vigilent controlled units
LSSE | 119702 | Unit 2 | Old Plantroom | AIRCON | AHU | ESHMTX | 51885 | 20KG OF R407C | 85 | Vigilent controlled units
LSSE | 119703 | Unit 3 | Old Plantroom | AIRCON | AHU | ESHMTX | 51886 | 20KG OF R407C | 85 | Vigilent controlled units
LSSE | 119704 | Unit 4 | New Plant Room | AIRCON | AHU | ESHMTX | 51888 | 20KG OF R407C | 85 | Vigilent controlled units
LSSE | 119705 | Unit 5 | Old Plantroom | AIRCON | AHU | ESHMTX | 51887 | 20KG OF R407C | 85 | Vigilent controlled units
LSSE | 119758 | Security office AC | Security Office | AIRCON | AHU | ESHMTX | 51903 | 1.9KG OF R410A | 8 | Used as and when required
LSSE | 510544 | Unit 6 | Compound | AIRCON | CHILLER | ESHMTX | 51889 | 12.5KG OF R410A | 70 | Vigilent controlled units
LSSE | 510545 | Unit 7 | Compound | AIRCON | CHILLER | ESHMTX | 51890 | 12.5KG OF R410A | 70 | Vigilent controlled units
SWW | VF 504021 | Liebert Unit No 4 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51466 | R407c 12.5 KG | 60
SWW | VF 504022 | Liebert Unit No 5 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51467 | R407c 12.5 KG | 60
SWW | VF 504023 | Liebert Unit No 6 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51468 | R407c 12.5KG | 60
SWW | VF-119068 | Control Room multi split | CONTROL ROOM | AIRCON | AHU | GCRMTX | 51470 | R407c 27KG | 60
SWW | VF504018 | Liebert Unit No 1 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51469 | R407c 12.5KG | 60
SWW | VF504019 | Liebert Unit No 2 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51464 | R407c 12.KG | 60
SWW | VF504020 | Liebert Unit No 3 | SWITCH ROOM | AIRCON | AHU | GCRMTX | 51465 | R407c 12.5 KG | 60
SC | VF - 120406 | Air Handling Unit No.1 |  | AIRCON | AHU | GLWMTX | 54522 | R407C 20.5Kg | 40
SC | VF - 120407 | Air Handling Unit No.2 |  | AIRCON | AHU | GLWMTX | 54523 | R407C 24.0Kg | 40
SC | VF - 120408 | Air Handling Unit No.3 |  | AIRCON | AHU | GLWMTX | 54524 | R407C 24.0Kg | 40
LNEA | 957807 | Security Office Split A/C Unit | Security Office | AIRCON | AHU | KCSMTX | 59188 | R410A 1.00kg | 3
LNEA | VF510763 | Air Handling Unit F1 | MTX 2 | AIRCON | AHU | KCSMTX | 60433 | R410A 48.1kg | 90
LNEA | VF510766 | Air Handling Unit F2 | MTX 2 | AIRCON | AHU | KCSMTX | 60435 | R410A 49.6kg | 81.8
LNEA | VF510769 | Air Handling Unit F3 | MTX 2 | AIRCON | AHU | KCSMTX | 60436 | R410A 51.6kg | 81.8
LNEA | VF510772 | Air Handling Unit F4 | MTX 2 | AIRCON | AHU | KCSMTX | 60437 | R410A 51.5kg | 81.8
LNEA | VF510775 | Air Handling Unit S1 | MTX 3 | AIRCON | AHU | KCSMTX | 60438 | R410A 48.3kg | 81.8
LNEA | VF510778 | Air Handling Unit S2 | MTX 3 | AIRCON | AHU | KCSMTX | 60439 | R410A 48.6kg | 81.8
LNEA | VF510781 | Air Handling Unit S3 | MTX 3 | AIRCON | AHU | KCSMTX | 60440 | R410A 45.2kg | 81.8
LNEA | VF510784 | Air Handling Unit S4 | MTX 3 | AIRCON | AHU | KCSMTX | 60441 | R410A 54.5kg | 81.8
LNEA | VF510787 | Air Handling Unit T1 | MTX 4 | AIRCON | AHU | KCSMTX | 60442 | R410A 43.5kg | 81.8
LNEA | VF510790 | Air Handling Unit T2 | MTX 4 | AIRCON | AHU | KCSMTX | 60444 | R410A 42.7kg | 81.8
LNEA | VF510793 | Air Handling Unit T3 | MTX 4 | AIRCON | AHU | KCSMTX | 60445 | R410A 45kg | 81.8
LNEA | VF510796 | Air Handling Unit T4 | MTX 4 | AIRCON | AHU | KCSMTX | 60443 | R410A 48.5kg | 81.8
Mids | 15468 | AHU - VAX ROOM |  | AIRCON | AHU | LCTMTX | 54123 | R410A - 1.7Kg | 7
Mids | 15469 | CONDENSER - VAX ROOM | EXTERNAL | AIRCON | CON | LCTMTX | 54124 | SEE ASSET 015468 | 7
Mids | 119207 | AHU 1 | PLANT ROOM | AIRCON | AHU | LCTMTX | 54117 | R407C - 25Kg 2x12.5 | 75
Mids | 119208 | AHU 2 | PLANT ROOM | AIRCON | AHU | LCTMTX | 54118 | R407C - 25Kg 2x12.5 | 75
Mids | 119209 | AHU 3 | PLANT ROOM | AIRCON | AHU | LCTMTX | 54119 | R407C - 25Kg 2x12.5 | 75
Mids | 119223 | CONDENSER - AHU 1 | COMPOUND | AIRCON | CON | LCTMTX | 54120 | SEE ASSET 119207 | 75
Mids | 119224 | CONDENSER - AHU 2 | COMPOUND | AIRCON | CON | LCTMTX | 54121 | SEE ASSET 119208 | 75
Mids | 119225 | CONDENSER - AHU 3 | COMPOUND | AIRCON | CON | LCTMTX | 54122 | SEE ASSET 119207 | 75
NE | VF-122322 | ACU 1 (2 x 3.6kg R407c) | EXTERNAL | AIRCON | AHU | LDSMTX | 51684 | R407C/2 x 3.6kg | 18
NE | VF-122323 | ACU 2 (2 x 3.6kg R407c) | EXTERNAL | AIRCON | AHU | LDSMTX | 51675 | R407C/2 x 3.6kg | 18
NE | VF-122324 | ACU 3 (2 x 3.6kg R407c) | EXTERNAL | AIRCON | AHU | LDSMTX | 51674 | R407C/2 x 3.6kg | 18
NE | VF-122325 | ACU 4 (2 x 3.6kg R407c) | EXTERNAL | AIRCON | AHU | LDSMTX | 51673 | R407C/ 2 x 3.6 | 18
SC | 50951 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60654 | R410A 1.0 Kg | 3.5
SC | 50952 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60653 | R410A 1.0 Kg | 3.5
SC | 50953 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60652 | R410A 1.0 Kg | 3.5
SC | 50954 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60658 | R410A 1.5 Kg | 5
SC | 50957 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60655 | R410A 1.0 Kg | 3.5
SC | 50958 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60656 | R410A 1.7 Kg | 8
SC | 50959 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60657 | R410A 1.7 Kg | 8
SC | 50960 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60659 | R410A 1.5 Kg | 5
SC | 50961 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60660 | R407C 4.4 Kg | 5
SC | 50962 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60664 | R407C 3.2 Kg | 8
SC | 50963 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60661 | R410A 1.62 Kg | 5
SC | 50965 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60662 | R410A 1.62 Kg | 5
SC | 50966 | DX Air Conditioning System | Side Chiller compound | AIRCON | AHU | LIVMTX | 60663 | R407C 4.0 Kg | 7
SC | CW - 050933 | Air Handling Unit No.2 | Main Equipment Room | AIRCON | FCU | LIVMTX | 54738 | Chilled Water | 78
SC | CW - 050936 | Air Handling Unit No.1 | Main Equipment Room | AIRCON | FCU | LIVMTX | 54737 | Chilled Water | 78
SC | CW - 050937 | Air Handling Unit No.3 | Main Equipment Room | AIRCON | FCU | LIVMTX | 54739 | Chilled Water | 78
SC | CW - 050938 | Air Handling Unit No.4 | Main Equipment Room | AIRCON | FCU | LIVMTX | 54741 | Chilled Water | 78
SC | CW - 050939 | Air Handling Unit No.5 | Main Equipment Room | AIRCON | FCU | LIVMTX | 54743 | Chilled Water | 78
SC | CW - 050939 | Air Handling Unit No.5 | Main Equipment Room | AIRCON | FCU | LIVMTX | 519311 | Chilled Water | 78
SC | VF - 111304 | Air Handling Unit No.6 |  | AIRCON | AHU | LIVMTX | 54745 | R407C | 99 | Decommissioned
NW | VF-502065 | AHU 1 | Switch room | AIRCON | AHU | LLDMTX | 60080 | R410 10KG | 78
NW | VF-502066 | AHU 2 | Switch room | AIRCON | AHU | LLDMTX | 60081 | R410 10KG | 78
NW | VF-502067 | AHU 3 | Switch room | AIRCON | AHU | LLDMTX | 60082 | R410 10KG | 78
NW | VF-502068 | AHU 4 | Switch room | AIRCON | AHU | LLDMTX | 60083 | R410 10KG | 78
NW | VF-502069 | AHU 5 | Switch room | AIRCON | AHU | LLDMTX | 60084 | R410 10KG | 78
NW | VF-502070 | AHU 6 | Switch room | AIRCON | AHU | LLDMTX | 60085 | R410 10KG | 78
NW | VF-502071 | AHU 7 | Switch room | AIRCON | AHU | LLDMTX | 60086 | R410 10KG | 78
NW | VF-502072 | AHU 8 | Switch room | AIRCON | AHU | LLDMTX | 60087 | R410 10KG | 78
NW |  | AHU 9 | Switch room | AIRCON | AHU | LLDMTX |  |  | 78
NW | VF-502073 | Chiller 1 | outside | AIRCON | CHILLER | LLDMTX | 60088 | R410 | 78
NW | VF-502074 | Chiller 2 | outside | AIRCON | CHILLER | LLDMTX | 60089 | R410 | 78
NW | VF-502075 | Chiller 3 | outside | AIRCON | CHILLER | LLDMTX | 60090 | R410 | 78
NW | VF-502076 | Chiller 4 | outside | AIRCON | CHILLER | LLDMTX | 60091 | R410 | 78
NW | VF-502077 | Chiller 5 | outside | AIRCON | CHILLER | LLDMTX | 60092 | R410 | 78
NW | VF-502078 | Chiller 6 | outside | AIRCON | CHILLER | LLDMTX | 60093 | R410 | 78
NW | VF-502079 | Chiller 7 | outside | AIRCON | CHILLER | LLDMTX | 60094 | R410 | 78
NW | VF-502079 | Chiller 8 | outside | AIRCON | CHILLER | LLDMTX |  |  | 78
Mids | 15363 | AHU 1 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53736 | Chilled Water | 78
Mids | 15364 | AHU 2 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53737 | Chilled Water | 78
Mids | 15365 | AHU 3 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53738 | Chilled Water | 78
Mids | 15366 | AHU 4 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53739 | Chilled Water | 78
Mids | 15367 | AHU 5 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53740 | Chilled Water | 78
Mids | 15368 | AHU 6 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53741 | Chilled Water | 78
Mids | 15369 | AHU 7 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53742 | Chilled Water | 78
Mids | 15370 | AHU 8 | SWITCH ROOM | AIRCON | FCU | MKSMTX | 53743 | Chilled Water | 78
Mids | 15371 | CHILLER 1 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53662 | R407C - 12.5Kg | 78
Mids | 15372 | CHILLER 2 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53706 | R407C - 12.5Kg | 78
Mids | 15373 | CHILLER 3 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53707 | R407C - 12.5Kg | 78
Mids | 15374 | CHILLER 4 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53708 | R407C - 12.5Kg | 78
Mids | 15375 | CHILLER 5 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53709 | R407C - 12.5Kg | 78
Mids | 15376 | CHILLER 6 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53711 | R407C - 12.5Kg | 78
Mids | 15377 | CHILLER 7 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53712 | R407C - 12.5Kg | 78
Mids | 15378 | CHILLER 8 | EXTERNAL | AIRCON | CHILLER | MKSMTX | 53713 | R407C - 12.5Kg | 78
Mids | VF510340 | CHILLER 9 | EXTERNAL | AIRCON | CHILLER | MKSMTX |  | R410A - 12.5Kg | 78 | VERTIV
Mids | 15387 | AHU 1A | CONTROL ROOM | AIRCON | AHU | MKSMTX | 53746 | R407C - 5.8Kg | 5
Mids | 15388 | AHU 1B | CONTROL ROOM | AIRCON | AHU | MKSMTX | 53747 | R407C - 3.1Kg | 2.5
Mids | 15389 | AHU 2 | CONTROL ROOM | AIRCON | AHU | MKSMTX | 53748 | R407C - 3.1Kg | 2
Mids | VF510339 | AHU 9 | SWITCH ROOM | AIRCON | FCU | MKSMTX |  |  | 80 | LIEBERT
Mids | 121493 | CONDENSER - AHU 2 | EXTERNAL | AIRCON | CON | MKSMTX | 53750 | SEE ASSET 015389 | 2.5
Mids | 121494 | CONDENSER - AHU 1 | EXTERNAL | AIRCON | CON | MKSMTX | 53749 | SEE ASSET 015387 | 5
Mids | 121498 | Fan Coil Unit No9 | EXTERNAL | AIRCON | CON | MKSMTX | 53745 | R407C 54Kg | 80
TVB | VF515051 | Test Lab unit 2 | CANAL TEST LAB | AIRCON | AHU | NBYMTX | 65115 | 4KG of R410A | 10
TVB | VF515053 | PABX AHU 3 | CANAL PABX ROOM | AIRCON | AHU | NBYMTX | 65116 | 4.9KG of R410A | 7.2
TVB | VF517549 | EXTRACT AHU INVERTOR TOP | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59788 |  |  | inverter/removed
TVB | VF517550 | EXTRACT AHU INVERTOR MIDDLE | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59792 |  |  | inverter/removed
TVB | VF517551 | EXTRACT AHU INVERTOR BOTTOM | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59791 |  |  | inverter/removed
TVB | VF517559 | SUPPLY INVERTOR | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59800 |  |  | inverter/removed
TVB | VF517560 | SUPPLY INVERTOR | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59801 |  |  | inverter/removed
TVB | VF517561 | SUPPLY INVERTOR | CANAL PLANT ROOM | AIRCON | FAU | NBYMTX | 59802 |  |  | inverter/removed
TVB | VF517569 | AIR CONDITIONING PANEL COP/1 | CANAL PLANT ROOM | AIRCON | DBD | NBYMTX | 59808 | 630 AMP ISOLATOR | 60 | distribution board
TVB | VF517599 | AHU EXTRACT | CANAL LOADING BAY | AIRCON | FAU | NBYMTX | 59838 |  | 60 | chilled water ahu/switched off
TVB | VF517605 | AHU SUPPLY | CANAL LOADING BAY | AIRCON | FAU | NBYMTX | 59839 |  | 60 | chilled water ahu/switched off
TVB | VF517656 | AHU 3 | CANAL COMPUTER ROOM 1 | AIRCON | AHU | NBYMTX | 59893 | R407C/20KG | 60
TVB | VF517657 | AHU 2 | CANAL COMPUTER ROOM 1 | AIRCON | AHU | NBYMTX | 59894 | R407C/20KG | 60
TVB | VF517658 | AHU 1 | CANAL COMPUTER ROOM 1 | AIRCON | AHU | NBYMTX | 59895 | R407C 20KG | 60
TVB | VF517660 | MTX CONTROL ROOM EXTRACT FAN | CANAL MTX CONTROL ROOM | AIRCON | FAU | NBYMTX | 59897 | 6 AMP |  | extract fan
TVB | VF517663 | MR SLIM SPILT | CANAL MTX CONTROL ROOM | AIRCON | AHU | NBYMTX | 59900 | R407C/5KG | 5
TVB | VF517664 | Air Handling Unit | CANAL MTX CONTROL ROOM | AIRCON | AHU | NBYMTX | 59901 | R407C/5KG | 5
TVB | VF517665 | AC UNIT 1 C1/C2 | CANAL SWITCH ROOM 2 | AIRCON | AHU | NBYMTX | 59902 | R407C 16.7KG/16.7KG | 100
TVB | VF517668 | MR SLIM CEILING MOUNTS AC/1 | CANAL PABX ROOM | AIRCON | AHU | NBYMTX | 59903 | R407C/4.9KG | 5
TVB | VF517670 | HITACHI | CANAL PATCH ROOM | AIRCON | AHU | NBYMTX | 59905 | R407C/2.8KG | 3
TVB | VF517674 | SANYO CEILING MOUNT | CANAL PABX ROOM | AIRCON | AHU | NBYMTX | 59909 | R407C/4.5KG | 5
TVB | VF517675 | SANYO CEILING MOUNT | CANAL PABX ROOM | AIRCON | AHU | NBYMTX | 59910 | R407C/4.5KG | 5
TVB | VF517683 | HITACHI | CANAL PATCH ROOM | AIRCON | AHU | NBYMTX | 59917 | R407C/5.1KG | 5
TVB | VF517684 | OFFICE CHILLED WATER UNIT C1/C2 | CANAL OUTSIDE COMPOUND | AIRCON | CHILLER | NBYMTX | 59918 | R407C/40KG X2 | 100 | non-operational
TVB | VF517806 | Airedale Blucube AHU 2 | CANAL MTX RM | AIRCON | AHU | NBYMTX | 62409 | R410A 16.5/16.8 KG | 70
TVB | VF517807 | Airedale Blucube AHU 1 | CANAL MTX RM | AIRCON | AHU | NBYMTX | 62410 | R410 17.5/17.5 KG | 70
NE | VF-122241 | AHU 1 | PLANT ROOM OUTSIDE COMPOUND | AIRCON | AHU | NWCMTX | 54047 | R407C/44.5 | 43
NE | VF-122242 | AHU 2 | PLANT ROOM OUTSIDE COMPOUND | AIRCON | AHU | NWCMTX | 54048 | R407C/38.6 | 43
NE | VF-122243 | AHU 3 | PLANT ROOM OUTSIDE COMPOUND | AIRCON | AHU | NWCMTX | 54049 | R407C | 43
NE | VF-122264 | Air Handling Unit 2 | SWITCH ROOM 2 | AIRCON | AHU | NWCMTX | 54021 | R407C | 50
NE | VF-122265 | Air Handling Unit 1 | SWITCH ROOM 2 | AIRCON | AHU | NWCMTX | 54022 | R407C | 50
NE | VF-122266 | Air Handling Unit 3 | SWITCH ROOM 2 | AIRCON | VENT | NWCMTX | 54023 | R407C | 50
NE | VF-122299 | VAX Room AHU | VAX ROOM | AIRCON | AHU | NWCMTX | 54035 | R407C/3.5 | 7
NE | VF-501523 | LIEBERT AHU 3 | SWITCH ROOM 3 | AIRCON | AHU | NWCMTX | 55364 | R410A/21 | 53
NE | VF-501524 | LIEBERT AHU 2 | SWITCH ROOM 3 | AIRCON | AHU | NWCMTX | 55363 | R410A/18.5 | 53
NE | VF-501525 | LIEBERT AHU 1 | SWITCH ROOM 3 | AIRCON | AHU | NWCMTX | 55362 | R410A/14.5 | 53
NE | VF-501533 | LIEBERT HBR99 Condenser AHU 1 | REAR COMPOUND | AIRCON | CON | NWCMTX | 55359 | R410A/14.5 | 53
NE | VF-501534 | LIEBERT HBR99 Condenser AHU 2 | REAR COMPOUND | AIRCON | CON | NWCMTX | 55360 | R410A/14.5 | 53
NE | VF-501535 | LIEBERT HBR099 Condenser AHU 3 | REAR COMPOUND | AIRCON | CON | NWCMTX | 55361 | R410A/14.5 | 53
NW | VF-121204 | Chiller 10 | outside | AIRCON | CHILLER | OLDMTX | 51639 | R410A | 78
NW | VF-121208 | Chiller 4 | outside | AIRCON | CHILLER | OLDMTX | 51699 | R410A | 78
NW | VF-121209 | Chiller 3 | outside | AIRCON | CHILLER | OLDMTX | 51700 | R410A | 78
NW | VF-121218 | Chiller 9 | outside | AIRCON | CHILLER | OLDMTX | 51637 | R410A | 78
NW | VF-121219 | Chiller 8 | outside | AIRCON | CHILLER | OLDMTX | 51636 | R410A | 78
NW | VF-121220 | Liebert DX Indoor Unit 7 |  | AIRCON | AHU | OLDMTX | 51635 | R407C 20.4KG | 78
NW | VF-121221 | Chiller 6 | outside | AIRCON | CHILLER | OLDMTX | 51634 | R410A | 78
NW | VF-121222 | Liebert DX Indoor Unit 5 |  | AIRCON | AHU | OLDMTX | 51633 | R407C 18.4KG | 78
NW | VF-121223 | Chiller 2 | outside | AIRCON | CHILLER | OLDMTX | 51638 | R410A | 78
NW | VF-121241 | Chiller 1 | outside | AIRCON | CHILLER | OLDMTX | 51802 | R410A | 78
TVB | VF-112474 | (OXFMTX) Liebert Unit No 4 | MTX 2 | AIRCON | AHU | OXFMTX | 51369 | R407c 28KG | 67 | IN STANDBY FOR ENERGY SAVING - READY TO USE IF NEEDED
TVB | VF-112475 | (OXFMTX) Liebert Unit No 5 | MTX 2 | AIRCON | AHU | OXFMTX | 51370 | R407c 28KG | 67 | In Use
TVB | VF-112476 | (OXFMTX) Liebert Unit No 6 | MTX 2 | AIRCON | AHU | OXFMTX | 51371 | R407c 28KG | 67 | In Use
TVB | VF-112502 | (OXFMTX) Liebert Unit No 13 | MTX 2 | AIRCON | AHU | OXFMTX | 51372 | NO GAS-DECOMMISSION | 67 | NO GAS-DECOMMISSION (IN MTX3 NOT MTX2)
TVB | VF-112503 | (OXFMTX) Liebert Unit No 14 | MTX 2 | AIRCON | AHU | OXFMTX | 51374 | RS44 8.5KG/8.9KG | 67 | NO GAS-DECOMMISSION (IN MTX3 NOT MTX2)
TVB | VF-112521 | (OXFMTX) MTX Supply Fan | Plantroom | AIRCON | FAU | OXFMTX | 51236 | Unknown | 3 | In Use
TVB | VF-112526 | (OXFMTX) Plantroom Supply Fan | Plantroom | AIRCON | FAU | OXFMTX | 51237 | Unknown | 3 | In Use
TVB | VF112537 | (OXFMTX) General Supply Fan | Plantroom | AIRCON | FAU | OXFMTX | 51235 | Unknown | 3 | In Use
TVB | VF-112560 | (OXFMTX) Toilet Extract Fan | Plantroom | AIRCON | FCU | OXFMTX | 51238 |  | 3 | SWITCHED OFF
TVB | VF-112561 | (OXFMTX) Extract Fan | Plantroom | AIRCON | FCU | OXFMTX | 51239 |  | 3 | SWITCHED OFF
TVB | VF-112562 | (OXFMTX) Extract Fan | Plantroom | AIRCON | FCU | OXFMTX | 51240 |  | 3 | SWITCHED OFF
TVB | VF-515011 | (OXFMTX) Chiller unit No1 indoor unit | MTX 1 | AIRCON | FAU | OXFMTX | 57807 |  | 20 | In Use
TVB | VF-515012 | (OXFMTX) Chiller unit No2 indoor unit | MTX 1 | AIRCON | FAU | OXFMTX | 57808 |  | 50 | In Use
TVB | VF-515013 | (OXFMTX) Chiller unit No3 indoor unit | MTX 1 | AIRCON | FAU | OXFMTX | 57809 |  | 20 | In Use
TVB | XOD Free cooling unit 1 | (OXFMTX) Emerson Free cooling Unit chiller 1 | MTX 1 | AIRCON | AHU | OXFMTX | 51366 | R410A 12.5KG | 50 | In Use
TVB | XOD Free Cooling Unit 2 | (OXFMTX) Emerson Free cooling Unit chiller 2 | MTX 1 | AIRCON | AHU | OXFMTX | 51367 | R410A 12.5KG | 50 | In Use
TVB | XOD Free Cooling Unit 3 | (OXFMTX) Emerson Free cooling Unit chiller 3 | MTX 1 | AIRCON | AHU | OXFMTX | 51368 | R410A 12.5KG | 50 | In Use
NE | VF-501501 | AHU-FC:03 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55189 | R410a/CHW | 78
NE | VF-501502 | AHU-FC:02 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55190 | R410a/CHW | 78
NE | VF-501503 | AHU-FC:01 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55191 | R410a/CHW | 78
NE | VF-501504 | AHU-FC:06 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55192 | R410a/CHW | 78
NE | VF-501505 | AHU-FC:05 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55193 | R410a/CHW | 78
NE | VF-501506 | AHU-FC:04 | MAINS POWER ROOM | AIRCON | FCU | RHMMTX | 55194 | R410a/CHW | 78
NE | VF-501508 | CONDENSOR CH:01 | MAINS POWER ROOM | AIRCON | CHILLER | RHMMTX | 55195 | R410a/12.5 | 78
NE | VF-501509 | CONDENSOR CH:02 | EXTERNAL | AIRCON | CHILLER | RHMMTX | 55196 | R410a/12.5 | 78
NE | VF-501510 | CONDENSOR CH:03 | MAINS POWER ROOM | AIRCON | CHILLER | RHMMTX | 55197 | R410a/12.5 | 78
NE | VF-501517 | CONDENSOR CH:04 | EXTERNAL | AIRCON | CHILLER | RHMMTX | 55302 | R410a/12.5 | 78
NE | VF-501518 | CONDENSOR CH:05 | EXTERNAL | AIRCON | CHILLER | RHMMTX | 55300 | R410a/12.5 | 78
NE | VF-501519 | CONDENSOR CH:06 | MAINS POWER ROOM | AIRCON | CHILLER | RHMMTX | 55296 | R410a/12.5 | 78
TVB | VF112312 | Office area supply fan | 1st Floor Office area | AIRCON | FAU | SHTMTX | 51061 | Unknown |  | ventilation fan
TVB | VF-112313 | MTX Supply Fan | Mtx Roof Void | AIRCON | FAU | SHTMTX | 51062 | Unknown |  | ventilation fan
TVB | VF-515043 | (SHT MTX) AHU 4 | GND floor MTX room | AIRCON | AHU | SHTMTX | 62309 | R410A 30KG | 83
TVB | VF-515044 | (SHT MTX) AHU 5 | GND floor MTX room | AIRCON | AHU | SHTMTX | 62310 | R410A 30KG | 83
TVB | VF-515045 | (SHT MTX) AHU 1 | GND floor MTX room | AIRCON | AHU | SHTMTX | 62306 | R410A 18KG | 83
TVB | VF-515046 | (SHT MTX) AHU 2 | GND floor MTX room | AIRCON | AHU | SHTMTX | 62307 | R410A 17KG | 83
TVB | VF-515047 | (SHT MTX) AHU 3 | GND floor MTX room | AIRCON | AHU | SHTMTX | 62308 | R410A 17KG | 83
LSSE | XSY Free cooling unit 1 | Emerson Free cooling Unit chiller 1 | MTX Room | AIRCON | AHU | SNYMTX | 52467 | 12.5KG OF R410A | 80 | In Use
LSSE | XSY free cooling unit 2 | Emerson Free cooling Unit chiller 2 | MTX Room | AIRCON | AHU | SNYMTX | 52468 | 12.5KG OF R410A | 80 | In Use
LSSE | XSY free cooling unit 3 | Emerson Free cooling Unit chiller 3 | MTX Room | AIRCON | AHU | SNYMTX | 52469 | 12.5KG OF R410A | 80 | In Use
LSSE | XSY free cooling unit 4 | Emerson Free cooling Unit chiller 4 | MTX Room | AIRCON | AHU | SNYMTX | 52470 | 12.5KG OF R410A | 80 | In Use
LSSE | XSY free cooling unit 5 | Emerson Free cooling Unit chiller 5 | MTX Room | AIRCON | AHU | SNYMTX | 52471 | 12.5KG OF R410A | 80 | In Use
LSSE | XSY free cooling unit 6 | Emerson Free cooling Unit chiller 6 | MTX Room | AIRCON | AHU | SNYMTX | 52472 | 12.5KG OF R410A | 80 | In Use
Mids | 21761 | AHU 1 | SWITCH ROOM | AIRCON | FCU | STDMTX | 55822 | CHILLED WATER | 78
Mids | 21762 | AHU 2 | SWITCH ROOM | AIRCON | AHU | STDMTX | 54941 | R410A - 17.6 +18.2Kg | 55
Mids | 21763 | AHU 3 | SWITCH ROOM | AIRCON | AHU | STDMTX | 54942 | R410A - 14.5 + 13Kg | 55
Mids | 21764 | AHU 4 | SWITCH ROOM | AIRCON | FCU | STDMTX | 54943 | CHILLED WATER | 78
Mids | 21777 | CHILLER 1 | COMPOUND | AIRCON | CHILLER | STDMTX | 54939 | R410A - 10.5Kg | 78
Mids | 21778 | CHILLER 4 | COMPOUND | AIRCON | CHILLER | STDMTX | 54940 | R410A - 10.5Kg | 78
Mids | 110005 | AHU 5 | SWITCH ROOM | AIRCON | AHU | STDMTX | 55850 | R407C - 35Kg | 81
Mids | 110006 | AHU 6 | SWITCH ROOM | AIRCON | AHU | STDMTX | 55851 | R407C - 35kg | 81
Mids | 120001 | AHU 1 | SITE GENERAL | AIRCON | AHU | WBYMTX | 52048 | R407C - 4.8kg | 18 | Site closed
Mids | 120002 | AHU 2 | SITE GENERAL | AIRCON | AHU | WBYMTX | 52049 | R407C - 4.8kg | 18 | Site closed
NW | VF-WTN 00001 | A/c no1 |  | AIRCON | AHU | WTNMTX | 54494 | R410 12.5KG | 60
NW | VF-WTN 00002 | A/c no2 |  | AIRCON | AHU | WTNMTX | 54495 | R410 12.5KG | 60
NW | VF-WTN 00003 | A/c no3 |  | AIRCON | AHU | WTNMTX | 54496 | R410 12.5KG | 60

## Dual Running Anaylsis (hidden)
Element Type | DC Load/Instance (kW) | Site Name | XAN | XBE | XCY | XEH | XER | XGR | XGL | XKS | XLD | XMS | XOM | XRM | XSN | XSY | Total Network Load (kW) | % of Type A Acutal Usage | Type A Total DC Design Capability (kW)
NGVM Core | 29 |  | XAN: 0; XBE: 1; XGL: 1; XLD: 1; XMS: 1 | 116 | #REF! | 4882.5
BBNS | 4 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  | 0 | 0 | 0 | #REF! | Type A Actual DC Usage (kW)
RNC's | 3 |  | 3 | 3 | 3 | 7 | 2 | 4 | 4 | 5 | 1 | 2 | 5 | 8 | 5 | 4 | 168 | #REF! | #REF!
BSC's | 3 |  | 3 | 6 | 3 | 7 | 2 | 4 | 4 | 4 | 5 | 6 | 4 | 4 | 2 | 4 | 174 | #REF! | Type A % of DC used to Support Dual Running Compared to Actual DC Usage
SMS | [16 empty] | 0 | #REF! | #REF!
Legacy IN | 3 |  | 5 | 2 | 6 | 4 | 5 | 5 | 5 | 4 | 4 | 6 | 6 | 7 | 8 | 5 | 216 | #REF! | Dual Running as % of Design Load
CHE | [16 empty] | 0 | #REF! | 14.3%
VML | 9 | [15 empty] | 0 | #REF!
CPN | 3 | [15 empty] | 24 | #REF! | bar: XBE; XEH; XGL to XRM
|  | Total Per Site (kW) | 33 | 65 | 36 | 57 | 27 | 39 | 71 | 42 | 62 | 74 | 48 | 60 | 45 | 39
|  | Overall Site Load (KW) | 170.7485 | 321.768 | 140.065 | 133.9065 | 114.3955 | 155.7065 | 228.464 | 197.072 | 189.3875 | 277.732 | 222.0875 | 151.4555 | 126.1675 | 154.1805
|  | % of Total Site Load | 19.33% | 20.2% | 25.7% | 42.57% | 23.6% | 25.05% | 31.08% | 21.31% | 32.74% | 26.64% | 21.61% | 39.62% | 35.67% | 25.3%
|  | Site Name | XAN | XBE | XCY | XEH | XER | XGR | XGL | XKS | XLD | XMS | XOM | XRM | XSN | XSY
|  | Dual Running (kW) | 33 | 65 | 36 | 57 | 27 | 39 | 71 | 42 | 62 | 74 | 48 | 60 | 45 | 39
|  | Site Load | 170.7485 | 321.768 | 140.065 | 133.9065 | 114.3955 | 155.7065 | 228.464 | 197.072 | 189.3875 | 277.732 | 222.0875 | 151.4555 | 126.1675 | 154.1805
|  | Site Load (kW) | 137.7485 | 256.768 | 104.065 | 76.9065 | 87.3955 | 116.7065 | 157.464 | 155.072 | 127.3875 | 203.732 | 174.0875 | 91.4555 | 81.1675 | 115.1805

## Dual Running (hidden)
Type A Sites - Dual Running Analysis (DC)
The top graph shows the % of a site's DC load attributed to dual running
The lower graph shows which network elements are dual running and the % they use across all Type A sites
Reducing the number of dual running elements could increase our DC capacity by 23%

## Rolling Figs (hidden)
Type A Graph data for 12 month Tech Load
Graphing Figs
MTX | Technology Load (kW) July 16 | Technology Load (kW) July 17 | Reserved Load (kW) | Forecast Load (kW) | Increase (kW) | Decrease (kW) | Difference (kW) |  |  | Technology Load (kW) July 16 | Technology Load (kW) July 17 | Reserved Load (kW) | Forecast Load (kW)
XAN | #REF! | 173.528 | 13.8975 | 1.526 |  | 10 | #REF!
XBE | #REF! | 372.671 | 39.022 | 57.6065 |  | 34 | #REF! |  | XEH | #REF!
XCY | #REF! | 126.44 | 0 | 8.066 |  |  | #REF! |  |  |  | 285.6345 | 50.0855 | 6.3765
XEH | #REF! | 285.6345 | 50.0855 | 6.3765 |  |  | #REF!
XER | #REF! | 83.0035 | 0 | 0 |  | 2 | #REF! |  | XER | #REF!
XGR | #REF! | 260.183 | 119.8455 | 31.5664 |  | 2 | #REF! |  |  |  | 83.0035 | 0 | 0
XGL | #REF! | #REF! | 67.3075 | 20.3884 |  | 40 | #REF!
XKS | #REF! | 127.4755 | 0 | 0 |  | 13 | #REF! |  | XKS | #REF!
XLD | #REF! | #REF! | 55.917 | 7.085 |  | 15 | #REF! |  |  |  | 127.4755 | 0 | 0
XMS | #REF! | 367.766 | 28.7215 | 46.107 |  | 10 | #REF!
XOM | #REF! | 293.21 | 105.5665 | 16.241 |  | 3 | #REF! |  | XSN | #REF!
XRM | #REF! | 100.2255 | 0 | 14.715 | 1 |  | #REF! |  |  |  | 95.3205 | 0 | 18.748
XSN | #REF! | 95.3205 | 0 | 18.748 |  | 3 | #REF!
XSY | #REF! | 111.7795 | 0 | 0 |  | 4 | #REF! |  | XSY | #REF!
Total | #REF! | #REF! | 480.363 | 228.4258 | 1 | 136 | #REF! |  |  |  | 111.7795 | 0 | 0
Total x9 | #REF! | #REF! | 430.2775 | 203.3013 | 1 | 114 | -113
Total x5 | #REF! | #REF! | 50.0855 | 25.1245 | 0 | 22 | -22
[9 empty] | Technology Load (kW) July 16 | Technology Load (kW) July 17 | Reserved Load (kW) | Forecast Load (kW)
| Type A Graph data for 12 month AC | [6 empty] | XBE | #REF!
[10 empty] | 372.671 | 39.022 | 57.6065
MTX | AC Load (kW) Mar 14 | AC Load (kW) Mar 15 | Difference (kW) | Increase (kW) | Decrease (kW)
XAN | 5 | 15 | 10 |  | -1 |  |  | XGL | #REF!
XBE | 122 | #REF! | #REF! |  | -34 |  |  |  |  | #REF! | 67.3075 | 20.3884
XCY | 14 | 8 | -6 |  | -4
XEH | 5 | #REF! | #REF! |  | -2 |  |  | XLD | #REF!
XER | 5 | #REF! | #REF! |  | -1 |  |  |  |  | #REF! | 55.917 | 7.085
XGR | 14 | 3.45 | -10.55 |  | -3
XGL | 58 | #REF! | #REF! |  | -1 |  |  | XMS | #REF!
XKS | 39 | #REF! | #REF! |  | -5 |  |  |  |  | 367.766 | 28.7215 | 46.107
XLD | 62 | #REF! | #REF! |  | -30
XMS | 60 | #REF! | #REF! |  | -7 |  |  | XAN | #REF!
XOM | 30 | 51 | 21 |  | -9 |  |  |  |  | 173.528 | 13.8975 | 1.526
XRM | 11 | 5 | -6 |  | -7
XSN | 13 | #REF! | #REF! |  | -5 |  |  | XCY | #REF!
XSY | 6 | 4 | -2 |  | -1 |  |  |  |  | 126.44 | 0 | 8.066
Total | 444 | #REF! | #REF! | 0 | -110
Total x8 | 371 | #REF! | -104.5 | 0 | -95 |  |  | XGR | #REF!
Total x6 | 73 | #REF! | -16.5 | 0 | -15 |  |  |  |  | 260.183 | 119.8455 | 31.5664
| Type B and C Graph data for 12 month DC | [6 empty] | XOM | #REF!
MTX | DC Load for the site (kW) Dec 12 | DC Load for the site (kW) Dec 13 | Migrations (kW) | Difference (kW) | Increase (kW) | Decrease (kW) |  |  |  | 293.21 | 105.5665 | 16.241
XBL | 36 | 43.8725 | 13 | 6 | 6
XCE | 39 | 45.998 |  | 6.998 | 0 |  |  | XRM | #REF!
XCF | 36 | 39.6215 |  | -4 |  | -4 |  |  |  | 100.2255 | 0 | 14.715
XCN | 19 | 38.15 | 21 | -1.85 | 2
TGW | 9 | 9.374 |  | 0.374 | 0
XHN | 22 | #REF! |  | #REF! |  | -3
XLR | 60 | 62.457 |  | 23 | 23
TLS | 7.1068 | #REF! |  | #REF! |  | -1
XNE | 46 | 44.472 |  | -3 |  | -3
XNY | 63 | 37.06 | 11 | 7 | 7
XOD | 22.7265 | 20.383 | 14 | -16.3435 |  | -9
XSD | 55 | 44.1995 | 18 | -28.8005 | 0
TWN | 44.0033 | 39.567 |  | -4.4363 |  | -3
TWY | 4.5998 | #REF! |  | -2 |  | -2
Total | 463.4364 | #REF! | 77 | #REF! | 38 | -25
Type B and C Graph data for 12 month AC
MTX | AC load for the site (kW) Jun 12 | AC load for the site (kW) July 13 | Difference (kW) | Increase (kW) | Decrease (kW) |  | 2012-09-01
XBL | 2.18 | 1.15 | -1.03 |  | -1 |  | 2
XCE | 2.18 | 1.15 | -1.03 |  |  |  | 2
XCN | 3.27 | 1.84 | -1.43 |  | -1 |  | 2
TGW | 0.2507 | 0.46 | 0.2093 |  |  | No data for XCF, XOD | 0.23
XHN | 1.09 | #REF! | #REF! |  |  |  | 1
XLR | 2.18 | 1.61 | -0.57 |  |  |  | 2
TLS | 0.2507 | #REF! | #REF! |  |  |  | 0.23
XNE | 2.18 | 1.38 | -0.8 |  |  |  | 2
XNY | 3.27 | 9.43 | 6.16 |  |  |  | 3
XSD | 3.27 | 1.61 | -1.66 |  | -1 |  | 3
TWN | 0.2507 | 0.69 | 0.4393 |  |  |  | 0.23
TWY | 0.2507 | #REF! | 0 |  |  |  | 0.23
Total | 20.3721 | #REF! | -3 |  | -3
Note on C10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Oct 16 Decreases inc Voicemail MTA, SMS-C, MCA and ACF cabs (11kW), then gradual decreases since
Note on B24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: (System Load)
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Multiply by 10% for load on DC plants

## ECO Mode (hidden)
MTX | Power Element Name | Power Element Type | Element Load (A) Jan 24 | Element Load (A) 25/02/24 | Total Running Site Load (kW)/(%) | Number of Modules | Module Capacity (kW) | Power Element Capability (kW) | Rectiifer Utilisation | Rectifier Utilisation | RectCap(A) | RecOutput (A) | ReqRect | ActCap (A) | SwitchOn | SwitchOff | MinRedundancy (%) | MaxRedundancy (%)
Acton | PEAAN | eSure | 622.998 | 629 | 173.528 | 36 | 3.5 | 126 | 28.68% | 50% | 60 | 30 | 21 | 1260 | 1200 | 1290 | 952 | 1102
Acton | PEBAN | eSure | 617.154 | 621 | 0 | 36 | 3.5 | 126 | 28.41% | 50% | 60 | 30 | 21 | 1260 | 1200 | 1290 | 965 | 1115
Acton | PECAN | eSure | 472.794 | 462 | 0 | 36 | 3.5 | 126 | 21.76% | 50% | 60 | 30 | 16 | 960 | 900 | 990 | 730 | 880
Acton | PEFAN | eSure | 701.839 | 713 | 0.55088 | 36 | 3.5 | 126 | 32.31% | 50% | 60 | 30 | 24 | 1440 | 1380 | 1470 | 1112 | 1262
Acton | PEGAN | eSure | 750.271 | 759 | 0 | 36 | 3.5 | 126 | 34.54% | 50% | 60 | 30 | 26 | 1560 | 1500 | 1590 | 1235 | 1385
Basingstoke | PEABE | eSure | 850.285 | 816 | 372.671 | 36 | 3.5 | 126 | 39.14% | 50% | 60 | 30 | 28 | 1680 | 1620 | 1710 | 1340 | 1490
Basingstoke | PEBBE | eSure | 829.374 | 840 | 0 | 36 | 3.5 | 126 | 38.18% | 50% | 60 | 30 | 28 | 1680 | 1620 | 1710 | 1300 | 1450
Basingstoke | PECBE | eSure | 920.886 | 809 | 0 | 36 | 3.5 | 126 | 42.39% | 50% | 60 | 30 | 27 | 1620 | 1560 | 1650 | 1252 | 1402
Basingstoke | PEEBE | eSure | 880.438 | 869 | 0 | 36 | 3.5 | 126 | 40.53% | 50% | 60 | 30 | 29 | 1740 | 1680 | 1770 | 1352 | 1502
Basingstoke | PEFBE | eSure | 853.706 | 847 | 0.73943 | 36 | 3.5 | 126 | 39.3% | 50% | 60 | 30 | 29 | 1740 | 1680 | 1770 | 1389 | 1539
Basingstoke | PEGBE | eSure | 864.712 | 878 | 0 | 36 | 3.5 | 126 | 39.8% | 50% | 60 | 30 | 30 | 1800 | 1740 | 1830 | 1437 | 1587
Basingstoke | PEHBE | eSure | 863.348 | 872 | 0 | 36 | 3.5 | 126 | 39.74% | 50% | 60 | 30 | 30 | 1800 | 1740 | 1830 | 1447 | 1597
Basingstoke | PEIBE | eSure | 889.778 | 907 | 0 | 36 | 3.5 | 126 | 40.96% | 50% | 60 | 30 | 31 | 1860 | 1800 | 1890 | 1489 | 1639
Crawley | PEACY | eSure | 388.804 | 391 | 126.44 | 36 | 3.5 | 126 | 17.9% | 50% | 60 | 30 | 14 | 840 | 780 | 870 | 649 | 799
Crawley | PEBCY | eSure | 496.376 | 497 | 0 | 36 | 3.5 | 126 | 22.85% | 50% | 60 | 30 | 17 | 1020 | 960 | 1050 | 772 | 922
Crawley | PECCY | eSure | 604.883 | 609 | 0 | 36 | 3.5 | 126 | 27.84% | 50% | 60 | 30 | 21 | 1260 | 1200 | 1290 | 985 | 1135
Crawley | PEDCY | eSure | 469.417 | 472 | 0.4014 | 36 | 3.5 | 126 | 21.61% | 50% | 60 | 30 | 16 | 960 | 900 | 990 | 714 | 864
Crawley | PEECY | eSure | 349.363 | 351 | 0 | 36 | 3.5 | 126 | 16.08% | 50% | 60 | 30 | 12 | 720 | 660 | 750 | 515 | 665
Edinburgh | PECEH | eSure | 845.371 | 836 | 285.6345 | 36 | 3.5 | 126 | 38.91% | 50% | 60 | 30 | 28 | 1680 | 1620 | 1710 | 1307 | 1457
Edinburgh | PEDEH | eSure | 913.211 | 899 | 0 | 36 | 3.5 | 126 | 42.04% | 50% | 60 | 30 | 30 | 1800 | 1740 | 1830 | 1402 | 1552
Edinburgh | PEEEH | eSure | 869.746 | 865 | 0 | 36 | 3.5 | 126 | 40.04% | 50% | 60 | 30 | 29 | 1740 | 1680 | 1770 | 1359 | 1509
Edinburgh | PEFEH | eSure | 834.984 | 824 | 0.75565 | 36 | 3.5 | 126 | 38.44% | 50% | 60 | 30 | 28 | 1680 | 1620 | 1710 | 1327 | 1477
Edinburgh | PEGEH | eSure | 925.312 | 944 | 0 | 36 | 3.5 | 126 | 42.59% | 50% | 60 | 30 | 32 | 1920 | 1860 | 1950 | 1527 | 1677
Esher | PEEER | eSure | 369.976 | 371 | 0 | 36 | 3.5 | 126 | 17.03% | 50% | 60 | 30 | 13 | 780 | 720 | 810 | 582 | 732
Esher | PEFER | eSure | 436.082 | 426 | 0.32938 | 36 | 3.5 | 126 | 20.07% | 50% | 60 | 30 | 15 | 900 | 840 | 930 | 690 | 840
Esher | PEGER | eSure | 308.471 | 311 | 0 | 36 | 3.5 | 126 | 14.2% | 50% | 60 | 30 | 11 | 660 | 600 | 690 | 482 | 632
Gloucester | PEAGR | eSure | 637.257 | 641 | 260.183 | 36 | 3.5 | 126 | 29.33% | 50% | 60 | 30 | 22 | 1320 | 1260 | 1350 | 1032 | 1182
Gloucester | PEBGR | eSure | 763.176 | 765 | 0 | 36 | 3.5 | 126 | 35.13% | 50% | 60 | 30 | 26 | 1560 | 1500 | 1590 | 1225 | 1375
Gloucester | PECGR | eSure | 715.404 | 716 | 0 | 36 | 3.5 | 126 | 32.93% | 50% | 60 | 30 | 24 | 1440 | 1380 | 1470 | 1107 | 1257
Gloucester | PEDGR | eSure | 713.649 | 711 | 0.55953 | 36 | 3.5 | 126 | 32.85% | 50% | 60 | 30 | 24 | 1440 | 1380 | 1470 | 1115 | 1265
Gloucester | PEEGR | eSure | 714.006 | 705 | 0 | 36 | 3.5 | 126 | 32.87% | 50% | 60 | 30 | 24 | 1440 | 1380 | 1470 | 1125 | 1275
Gravelly Hill | BMGMTX-DCSYS01 | HDR48-ES | 757 | 766 | 295.172 | 44 | 3 | 132 | 33.26% | 50% | 51 | 25.5 | 31 | 1581 | 1530 | 1606.5 | 1499 | 1649
Gravelly Hill | BMGMTX-DCSYS02 | HDR48-ES | 785 | 785 | 0 | 44 | 3 | 132 | 34.49% | 50% | 51 | 25.5 | 31 | 1581 | 1530 | 1606.5 | 1461 | 1611
Gravelly Hill | PECGL | eSure | 784 | 858 | 0 | 36 | 3.5 | 126 | 36.09% | 50% | 60 | 30 | 29 | 1740 | 1680 | 1770 | 1370 | 1520
Gravelly Hill | BMGMTX-DCSYS04 | HDR48-ES | 810 | 797 | 0.6389 | 44 | 3.5 | 132 | 30.51% | 50% | 60 | 30 | 27 | 1620 | 1560 | 1650 | 1272 | 1422
Gravelly Hill | BMGMTX-DCSYS05 | HDR48-ES | 797 | 799 | 0 | 44 | 3 | 132 | 35.02% | 50% | 51 | 25.5 | 32 | 1632 | 1581 | 1657.5 | 1534 | 1684
Gravelly Hill | PEFGL | eSure | 828 | 844 | 0 | 36 | 3.5 | 126 | 38.11% | 50% | 60 | 30 | 29 | 1740 | 1680 | 1770 | 1394 | 1544
Kings Cross | PEAKS | eSure | 257.309 | 248 | 127.4755 | 24 | 3.5 | 84 | 17.77% | 50% | 60 | 30 | 9 | 540 | 480 | 570 | 387 | 537
Kings Cross | PEBKS | eSure | 358.273 | 352 | 0 | 30 | 3.5 | 105 | 19.79% | 50% | 60 | 30 | 12 | 720 | 660 | 750 | 514 | 664
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Kings Cross | PEEKS | eSure | 101.516 | 100 | 0 | 12 | 3.5 | 42 | 14.02% | 50% | 60 | 30 | 4 | 240 | 180 | 270 | 134 | 284
Kings Cross | PEIKS | eSure | 531.315 | 528 | 0 | 36 | 3.5 | 126 | 24.46% | 50% | 60 | 30 | 18 | 1080 | 1020 | 1110 | 820 | 970
Kings Cross | PEJKS | eSure | 315 | 229 | 0 | 36 | 3.5 | 126 | 14.5% | 50% | 60 | 30 | 8 | 480 | 420 | 510 | 319 | 469
Kings Cross | PEKKS | eSure | 526.933 | 484 | 0.32029 | 30 | 3.5 | 105 | 29.11% | 50% | 60 | 30 | 17 | 1020 | 960 | 1050 | 794 | 944
Kings Cross | PELKS | eSure | 162.224 | 161 | 0 | 24 | 3.5 | 84 | 11.2% | 50% | 60 | 30 | 6 | 360 | 300 | 390 | 232 | 382
Kings Cross | PEMKS | eSure | 146.784 | 146 | 0 | 24 | 3.5 | 84 | 10.14% | 50% | 60 | 30 | 5 | 300 | 240 | 330 | 157 | 307
Kings Cross | PENKS | eSure | 100.584 | 91 | 0 | 12 | 3.5 | 42 | 13.89% | 50% | 60 | 30 | 4 | 240 | 180 | 270 | 149 | 299
Leyland | LLDMTX-DCSYS01 | HDR48-ES | 907 | 901 | 331.251 | 44 | 3 | 132 | 39.85% | 50% | 51 | 25.5 | 36 | 1836 | 1785 | 1861.5 | 1734 | 1884
Leyland | LLDMTX-DCSYS02 | HDR48-ES | 805 | 810 | 0 | 44 | 3 | 132 | 35.37% | 50% | 51 | 25.5 | 32 | 1632 | 1581 | 1657.5 | 1512 | 1662
Leyland | LLDMTX-DCSYS03 | HDR48-ES | 934 | 929 | 0 | 44 | 3 | 132 | 41.04% | 50% | 51 | 25.5 | 37 | 1887 | 1836 | 1912.5 | 1779 | 1929
Leyland | LLDMTX-DCSYS04 | HDR48-ES | 860 | 859 | 0.72011 | 44 | 3 | 132 | 37.79% | 50% | 51 | 25.5 | 34 | 1734 | 1683 | 1759.5 | 1616 | 1766
Leyland | LLDMTX-DCSYS05 | HDR48-ES | 909 | 910 | 0 | 44 | 3 | 132 | 39.94% | 50% | 51 | 25.5 | 36 | 1836 | 1785 | 1861.5 | 1716 | 1866
Leyland | LLDMTX-DCSYS06 | HDR48-ES | 900 | 898 | 0 | 44 | 3 | 132 | 39.55% | 50% | 51 | 25.5 | 36 | 1836 | 1785 | 1861.5 | 1740 | 1890
Milton Keynes | PEAMS | eSure | 1047.611 | 1046 | 367.766 | 42 | 3.5 | 147 | 41.33% | 50% | 60 | 30 | 35 | 2100 | 2040 | 2130 | 1657 | 1807
Milton Keynes | PEBMS | eSure | 989.083 | 988 | 0 | 42 | 3.5 | 147 | 39.03% | 50% | 60 | 30 | 33 | 1980 | 1920 | 2010 | 1554 | 1704
Milton Keynes | PECMS | eSure | 960.893 | 960 | 0 | 42 | 3.5 | 147 | 37.91% | 50% | 60 | 30 | 32 | 1920 | 1860 | 1950 | 1500 | 1650
Milton Keynes | PEDMS | eSure | 1132.436 | 1131 | 0.76618 | 42 | 3.5 | 147 | 44.68% | 50% | 60 | 30 | 38 | 2280 | 2220 | 2310 | 1815 | 1965
Milton Keynes | PEEMS | eSure | 1058.541 | 1051 | 0 | 42 | 3.5 | 147 | 41.77% | 50% | 60 | 30 | 36 | 2160 | 2100 | 2190 | 1749 | 1899
Milton Keynes | PEFMS | eSure | 1041.864 | 1045 | 0 | 42 | 3.5 | 147 | 41.11% | 50% | 60 | 30 | 35 | 2100 | 2040 | 2130 | 1659 | 1809
Oldham | OLDMTX-DCSYS01 | HDR48-ES | 891 | 887 | 293.21 | 44 | 3 | 132 | 39.15% | 50% | 51 | 25.5 | 35 | 1785 | 1734 | 1810.5 | 1661 | 1811
Oldham | OLDMTX-DCSYS02 | HDR48-ES | 820 | 818 | 0 | 44 | 3 | 132 | 36.03% | 50% | 51 | 25.5 | 33 | 1683 | 1632 | 1708.5 | 1597 | 1747
Oldham | OLDMTX-DCSYS03 | HDR48-ES | 822 | 820 | 0 | 44 | 3 | 132 | 36.12% | 50% | 51 | 25.5 | 33 | 1683 | 1632 | 1708.5 | 1593 | 1743
Oldham | OLDMTX-DCSYS04 | HDR48-ES | 621 | 615 | 0.63056 | 34 | 3 | 102 | 35.31% | 50% | 51 | 25.5 | 25 | 1275 | 1224 | 1300.5 | 1195 | 1345
Oldham | OLDMTX-DCSYS05 | HDR48-ES | 636 | 637 | 0 | 44 | 3 | 132 | 27.95% | 50% | 51 | 25.5 | 25 | 1275 | 1224 | 1300.5 | 1151 | 1301
Oldham | OLDMTX-DCSYS06 | HDR48-ES | 646 | 652 | 0 | 44 | 3 | 132 | 28.38% | 50% | 51 | 25.5 | 26 | 1326 | 1275 | 1351.5 | 1222 | 1372
Rotherham | PEARM | eSure | 400.468 | 401 | 100.2255 | 36 | 3.5 | 126 | 18.43% | 50% | 60 | 30 | 14 | 840 | 780 | 870 | 632 | 782
Rotherham | PEBRM | eSure | 437.985 | 437 | 0 | 36 | 3.5 | 126 | 20.16% | 50% | 60 | 30 | 15 | 900 | 840 | 930 | 672 | 822
Rotherham | PECRM | eSure | 532.697 | 533 | 0 | 36 | 3.5 | 126 | 24.52% | 50% | 60 | 30 | 18 | 1080 | 1020 | 1110 | 812 | 962
Rotherham | PEDRM | eSure | 255.944 | 256 | 0.31818 | 36 | 3.5 | 126 | 11.78% | 50% | 60 | 30 | 9 | 540 | 480 | 570 | 374 | 524
Rotherham | PEERM | eSure | 211.459 | 212 | 0 | 36 | 3.5 | 126 | 9.734% | 50% | 60 | 30 | 8 | 480 | 420 | 510 | 347 | 497
Southampton | PEASN | eSure | 385 | 368 | 95.3205 | 36 | 3.5 | 126 | 17.72% | 50% | 60 | 30 | 13 | 780 | 720 | 810 | 587 | 737
Southampton | PEBSN | eSure | 562 | 544 | 0 | 36 | 3.5 | 126 | 25.87% | 50% | 60 | 30 | 19 | 1140 | 1080 | 1170 | 894 | 1044
Southampton | PECSN | eSure | 497 | 491 | 0.37826 | 36 | 3.5 | 126 | 22.88% | 50% | 60 | 30 | 17 | 1020 | 960 | 1050 | 782 | 932
Southampton | PEESN | eSure | 353 | 346 | 0 | 36 | 3.5 | 126 | 16.25% | 50% | 60 | 30 | 12 | 720 | 660 | 750 | 524 | 674
Swanley | PEASY | eSure | 544.639 | 538 | 111.7795 | 36 | 3.5 | 126 | 25.07% | 50% | 60 | 30 | 18 | 1080 | 1020 | 1110 | 804 | 954
Swanley | PEBSY | eSure | 469.683 | 498 | 0 | 36 | 3.5 | 126 | 21.62% | 50% | 60 | 30 | 17 | 1020 | 960 | 1050 | 770 | 920
Swanley | PECSY | eSure | 384.775 | 384 | 0 | 36 | 3.5 | 126 | 17.71% | 50% | 60 | 30 | 13 | 780 | 720 | 810 | 560 | 710
Swanley | PEDSY | eSure | 296.403 | 298 | 0.3677 | 36 | 3.5 | 126 | 13.64% | 50% | 60 | 30 | 10 | 600 | 540 | 630 | 404 | 554
Swanley | PEESY | eSure | 311.686 | 333 | 0 | 30 | 3.5 | 105 | 17.22% | 50% | 60 | 30 | 12 | 720 | 660 | 750 | 545 | 695
Bristol | PEFBL | NetSure | 473.663 | 476 | 43.8725 | 36 | 3.2 | 115 | 23.85% | 50% | 55 | 27.5 | 18 | 990 | 935 | 1017.5 | 835 | 985
Bristol | PEHBL | NetSure | 330.273 | 329 | 0 | 36 | 3.2 | 115 | 16.63% | 50% | 55 | 27.5 | 12 | 660 | 605 | 687.5 | 502 | 652
Cardiff | PECCF | NetSure | 348.906 | 352 | 39.6215 | 36 | 3.2 | 115 | 17.57% | 50% | 55 | 27.5 | 13 | 715 | 660 | 742.5 | 560 | 710
Cardiff | PEDCF | NetSure | 165.07 | 165 | 0 | 18 | 3.2 | 57 | 16.62% | 50% | 55 | 27.5 | 6 | 330 | 275 | 357.5 | 200 | 350
Cardiff | PEECF | NetSure | 209.479 | 210 | 0 | 18 | 3.2 | 57 | 21.09% | 50% | 55 | 27.5 | 8 | 440 | 385 | 467.5 | 319 | 469
Carlisle | PEACE | NetSure | 400 | 400 | 45.998 | 36 | 3.2 | 115 | 20.14% | 50% | 55 | 27.5 | 15 | 825 | 770 | 852.5 | 673 | 823
Carlisle | PEBCE | NetSure | 439 | 444 | 0 | 36 | 3.2 | 115 | 22.1% | 50% | 55 | 27.5 | 17 | 935 | 880 | 962.5 | 793 | 943
Croydon | PEFCN | NetSure | 313 | 313 | 38.15 | 36 | 3.2 | 115 | 15.76% | 50% | 55 | 27.5 | 12 | 660 | 605 | 687.5 | 531 | 681
Croydon | PEGCN | NetSure | 389 | 387 | 0 | 36 | 3.2 | 115 | 19.59% | 50% | 55 | 27.5 | 15 | 825 | 770 | 852.5 | 697 | 847
Glasgow TXO | PEJGW | eSure | 86 | 87 | 9.374 | 9 | 3.5 | 31 | 15.83% | 50% | 60 | 30 | 3 | 180 | 120 | 210 | 55 | 205
Glasgow TXO | PEKGW | eSure | 84 | 85 | 0 | 9 | 3.5 | 31 | 15.47% | 50% | 60 | 30 | 3 | 180 | 120 | 210 | 59 | 209
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Leicester | PEFLR | NetSure | 626 | 626 | 62.457 | 36 | 3.2 | 115 | 31.52% | 50% | 55 | 27.5 | 23 | 1265 | 1210 | 1292.5 | 1062 | 1212
Leicester | PEGLR | NetSure | 519 | 520 | 0 | 36 | 3.2 | 115 | 26.13% | 50% | 55 | 27.5 | 19 | 1045 | 990 | 1072.5 | 855 | 1005
Newbury | PEGNY | NetSure | 366 | 366 | 37.06 | 36 | 3.2 | 115 | 18.43% | 50% | 55 | 27.5 | 14 | 770 | 715 | 797.5 | 635 | 785
Newbury | PEHNY | NetSure | 312 | 314 | 0 | 36 | 3.2 | 115 | 15.71% | 50% | 55 | 27.5 | 12 | 660 | 605 | 687.5 | 530 | 680
#REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | 150% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | 250% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Newcastle | PEENE | NetSure | 306 | 306 | 44.472 | 36 | 3.2 | 115 | 15.41% | 50% | 55 | 27.5 | 12 | 660 | 605 | 687.5 | 544 | 694
Newcastle | PEFNE | NetSure | 361 | 359 | 0 | 36 | 3.2 | 115 | 18.18% | 50% | 55 | 27.5 | 14 | 770 | 715 | 797.5 | 648 | 798
Newcastle | PEGNE | NetSure | 147 | 151 | 0 | 18 | 3.2 | 57 | 14.8% | 50% | 55 | 27.5 | 6 | 330 | 275 | 357.5 | 226 | 376
Oxford | PECOD | NetSure | 236 | 236 | 20.383 | 36 | 3.2 | 115 | 11.88% | 50% | 55 | 27.5 | 9 | 495 | 440 | 522.5 | 371 | 521
Oxford | PEFOD | NetSure | 138 | 138 | 0 | 30 | 3.2 | 96 | 8.338% | 50% | 55 | 27.5 | 6 | 330 | 275 | 357.5 | 250 | 400
Stafford | PEESD | NetSure | 380 | 394 | 44.1995 | 36 | 3.2 | 115 | 19.13% | 50% | 55 | 27.5 | 15 | 825 | 770 | 852.5 | 684 | 834
Stafford | PEGSD | NetSure | 447 | 417 | 0 | 36 | 3.2 | 115 | 22.51% | 50% | 55 | 27.5 | 16 | 880 | 825 | 907.5 | 742 | 892
Warrington TXO | PELWN | NetSure | 208.912 | 209 | 39.567 | 18 | 3.2 | 57 | 21.04% | 50% | 55 | 27.5 | 8 | 440 | 385 | 467.5 | 320 | 470
Warrington TXO | PEMWN | NetSure | 156.163 | 156 | 0 | 18 | 3.2 | 57 | 15.72% | 50% | 55 | 27.5 | 6 | 330 | 275 | 357.5 | 217 | 367
Warrington TXO | PENWN | NetSure | 360.743 | 361 | 0 | 18 | 3.2 | 57 | 36.32% | 50% | 55 | 27.5 | 14 | 770 | 715 | 797.5 | 644 | 794
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 50% | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Rectifier Reduction (hidden)
MTX | Plant Name | Load (A) | Physical Rectifier Count | Load per Rectifier (A) | Power Output Per Rectifier (W) | NetSure Rectifier Effiency (%) | Total Load on Building (kW) | NetSure (with ECO) Theoretical Best (kW) | NetSure Delta (kW) - With ECO | NetSure (With ECO) Financial Saving | eSure Rectifier Efficency (%) -No ECO | eSure Load on building (kW) - No Eco | NetSure to eSure Delta (kW) - No ECO | eSure (no ECO) Financial Saving | eSure Theoretical Best (kW) | NetSure to eSure Delta (kW) - With ECO | eSure (with ECO) Financial Saving
Acton | PEAAN | 629 | 36 | 17.4722 | 952.2361 | 90.7451 | 37.4531 | 37.0229 | 0.43017 | 486.4862 | 95.5 | 35.8231 | 1.63 | 1843.379 | 35.3089 | 2.1442 | 2424.9045 | Vout（V) | Iout(A) | Pin(W) | Pout(W) | Efficiency(%)
Acton | PEBAN | 621 | 36 | 17.25 | 940.125 | 90.7451 | 36.9768 | 36.5521 | 0.4247 | 480.2987 | 95.5 | 35.3675 | 1.6093 | 1819.9338 | 34.8598 | 2.1169 | 2394.0631 | 57.039 | 3.026 | 230.4 | 172.6 | 74.9132
Acton | PECAN | 462 | 36 | 12.8333 | 699.4167 | 88.5162 | 28.0705 | 27.1933 | 0.87718 | 992.0136 | 95 | 26.438 | 1.6325 | 1846.2736 | 25.9344 | 2.1361 | 2415.7803 | 57.032 | 5.031 | 349.6 | 286.928 | 82.0732
Acton | PEFAN | 713 | 36 | 19.8056 | 1079.4028 | 90.7451 | 42.4548 | 41.9672 | 0.48762 | 551.4541 | 96 | 40.4128 | 2.042 | 2309.2821 | 40.0243 | 2.4305 | 2748.7391 | 57.013 | 10.028 | 645.9 | 571.7264 | 88.5162
Acton | PEGAN | 759 | 36 | 21.0833 | 1149.0417 | 91.7414 | 44.7817 | 44.6747 | 0.10697 | 120.9728 | 96 | 0 | 0 | 0 | 42.6065 | 2.1752 | 2460.0181 | 56.995 | 14.987 | 941.3 | 854.1841 | 90.7451
Crawley | PEACY | 391 | 36 | 10.8611 | 591.9306 | 88.5162 | 23.7566 | 23.0143 | 0.74237 | 839.5613 | 93 | 22.8012 | 0.95547 | 1080.5539 | 21.9488 | 1.8078 | 2044.524 | 56.976 | 20 | 1242.1 | 1139.52 | 91.7414
Crawley | PEBCY | 497 | 36 | 13.8056 | 752.4028 | 88.5162 | 30.197 | 29.2534 | 0.94363 | 1067.1662 | 95 | 28.4408 | 1.7562 | 1986.1429 | 27.8991 | 2.298 | 2598.794 | 56.946 | 25.006 | 1541 | 1423.9917 | 92.407
Crawley | PECCY | 609 | 36 | 16.9167 | 921.9583 | 90.7451 | 36.2622 | 35.8457 | 0.41649 | 471.0176 | 95.5 | 34.6841 | 1.5782 | 1784.766 | 34.1862 | 2.076 | 2347.801 | 56.929 | 30.01 | 1852.4 | 1708.4393 | 92.2284
Crawley | PEDCY | 472 | 36 | 13.1111 | 714.5556 | 88.5162 | 28.6781 | 27.7819 | 0.89616 | 1013.4858 | 95 | 27.0102 | 1.6679 | 1886.2363 | 26.4957 | 2.1824 | 2468.0699 | 56.917 | 35.074 | 2166 | 1996.3069 | 92.1656
Crawley | PEECY | 351 | 36 | 9.75 | 531.375 | 82.0732 | 22.5588 | 20.6599 | 1.8989 | 2147.5445 | 93 | 20.4686 | 2.0902 | 2363.8831 | 19.7034 | 2.8554 | 3229.2374 | 56.9 | 40.103 | 2477 | 2281.8607 | 92.1219
Edinburgh | PECEH | 836 | 36 | 23.2222 | 1265.6111 | 91.7414 | 49.3248 | 49.207 | 0.11782 | 133.2454 | 96 | 47.3845 | 1.9403 | 2194.3172 | 46.9289 | 2.3959 | 2709.5851 | 56.881 | 45.073 | 2788 | 2563.7973 | 91.9583
Edinburgh | PEDEH | 899 | 36 | 24.9722 | 1360.9861 | 91.7414 | 53.0418 | 52.9151 | 0.1267 | 143.2866 | 96 | 50.9553 | 2.0865 | 2359.6784 | 50.4654 | 2.5765 | 2913.7763 | 56.861 | 50.099 | 3105 | 2848.6792 | 91.7449
Edinburgh | PEEEH | 865 | 36 | 24.0278 | 1309.5139 | 91.7414 | 51.0358 | 50.9139 | 0.12191 | 137.8675 | 96 | 49.0282 | 2.0076 | 2270.4358 | 48.5568 | 2.479 | 2803.5779 | 56.83 | 56.156 | 3496 | 3191.3455 | 91.2856
Edinburgh | PEFEH | 824 | 36 | 22.8889 | 1247.4444 | 91.7414 | 48.6168 | 48.5006 | 0.11613 | 131.3327 | 96 | 46.7043 | 1.9124 | 2162.8198 | 46.2552 | 2.3615 | 2670.6915
Edinburgh | PEGEH | 944 | 36 | 26.2222 | 1429.1111 | 92.407 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0
Esher | PEDER | 415 | 36 | 11.5278 | 628.2639 | 88.5162 | 25.2148 | 24.4269 | 0.78794 | 891.0945 | 93 | 24.2007 | 1.0141 | 1146.8794 | 23.296 | 1.9188 | 2170.0191
Esher | PEEER | 371 | 36 | 10.3056 | 561.6528 | 82.0732 | 23.8442 | 21.8371 | 2.0071 | 2269.9117 | 93 | 21.6349 | 2.2093 | 2498.5773 | 20.8261 | 3.0181 | 3413.2395 |  | Electrical unit Price (pkWh) | 0.1291
Esher | PEFER | 426 | 36 | 11.8333 | 644.9167 | 88.5162 | 25.8832 | 25.0744 | 0.80883 | 914.7139 | 93 | 24.8422 | 1.041 | 1177.2786 | 23.9135 | 1.9697 | 2227.5377
Esher | PEGER | 311 | 36 | 8.6389 | 470.8194 | 82.0732 | 19.988 | 18.3055 | 1.6825 | 1902.8101 | 91 | 18.475 | 1.513 | 1711.1255 | 17.458 | 2.53 | 2861.2331
Gloucester | PEAGR | 641 | 36 | 17.8056 | 970.4028 | 90.7451 | 38.1676 | 37.7293 | 0.43838 | 495.7673 | 95.5 | 36.5066 | 1.6611 | 1878.5468 | 35.9825 | 2.1851 | 2471.1665
Gloucester | PEBGR | 765 | 36 | 21.25 | 1158.125 | 91.7414 | 45.1357 | 45.0279 | 0.10781 | 121.9291 | 96 | 43.3602 | 1.7755 | 2007.9577 | 42.9433 | 2.1924 | 2479.4648
Gloucester | PECGR | 716 | 36 | 19.8889 | 1083.9444 | 90.7451 | 42.6334 | 42.1438 | 0.48967 | 553.7744 | 96 | 40.5829 | 2.0505 | 2318.9986 | 40.1927 | 2.4408 | 2760.3046
Gloucester | PEDGR | 711 | 36 | 19.75 | 1076.375 | 90.7451 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0
Gloucester | PEEGR | 705 | 36 | 19.5833 | 1067.2917 | 90.7451 | 41.9784 | 41.4963 | 0.48215 | 545.2667 | 96 | 39.9594 | 2.019 | 2283.3715 | 39.5752 | 2.4033 | 2717.8977
Kings Cross | PEAKS | 248 | 24 | 10.3333 | 563.1667 | 82.0732 | 15.939 | 14.5973 | 1.3417 | 1517.3534 | 93 | 14.4621 | 1.4769 | 1670.208 | 13.9215 | 2.0175 | 2281.6264
Kings Cross | PEBKS | 352 | 30 | 11.7333 | 639.4667 | 88.5162 | 21.387 | 20.7187 | 0.66833 | 755.8199 | 93 | 20.5269 | 0.86017 | 972.7748 | 19.7595 | 1.6275 | 1840.5945 |  | Type A (NetSure with ECO)
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Total Load on Building (kW) | Theoretical best (kW) | Delta (kW) | Financial Saving
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF!
Kings Cross | PEEKS | 100 | 12 | 8.3333 | 454.1667 | 82.0732 | 6.427 | 5.886 | 0.54101 | 611.836 | 91 | 5.9405 | 0.48651 | 550.2011 | 5.6135 | 0.81351 | 920.0107
Kings Cross | PEIKS | 528 | 36 | 14.6667 | 799.3333 | 88.5162 | 32.0806 | 31.0781 | 1.0025 | 1133.7299 | 95 | 30.2148 | 1.8658 | 2110.027 | 29.6393 | 2.4413 | 2760.8918 |  | Type A (eSure with ECO)
Kings Cross | PEJKS | 229 | 36 | 6.3611 | 346.6806 | 82.0732 | 14.7179 | 13.4789 | 1.2389 | 1401.1046 | #N/A | #N/A | #N/A | #N/A | 12.8549 | 1.8629 | 2106.8244 |  | Total Load on Building (kW) | Theoretical best (kW) | Delta (kW) | Financial Saving
Kings Cross | PEKKS | 484 | 30 | 16.1333 | 879.2667 | 90.7451 | 28.8192 | 28.4882 | 0.33101 | 374.3391 | 95.5 | 27.565 | 1.2542 | 1418.4347 | 27.1693 | 1.6499 | 1865.9042 |  |  |  | #REF! | #REF!
Kings Cross | PELKS | 161 | 24 | 6.7083 | 365.6042 | 82.0732 | 10.3475 | 9.4765 | 0.87102 | 985.056 | 91 | 9.5642 | 0.78328 | 885.8238 | 9.0377 | 1.3097 | 1481.2172
Kings Cross | PEMKS | 146 | 24 | 6.0833 | 331.5417 | 82.0732 | 9.3834 | 8.5936 | 0.78987 | 893.2806 | #N/A | #N/A | #N/A | #N/A | 8.1957 | 1.1877 | 1343.2156 |  | Type A (eSure without ECO)
Kings Cross | PENKS | 91 | 12 | 7.5833 | 413.2917 | 82.0732 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Load on Building (kW) |  | Delta (kW) | Financial Saving
Oldham | OLDMTX-DCSYS01 | 887 | 44 | 20.1591 | 1098.6705 | 90.7451 | 52.8154 | 52.2088 | 0.60661 | 686.0306 | 96 | 50.2752 | 2.5403 | 2872.8376 | 49.7917 | 3.0237 | 3419.5393 |  | #REF! |  | #REF! | #REF!
Oldham | OLDMTX-DCSYS02 | 818 | 44 | 18.5909 | 1013.2045 | 90.7451 | 48.7069 | 48.1475 | 0.55943 | 632.664 | 95.5 | 46.5871 | 2.1198 | 2397.2718 | 45.9184 | 2.7885 | 3153.5323
Oldham | OLDMTX-DCSYS03 | 820 | 44 | 18.6364 | 1015.6818 | 90.7451 | 48.826 | 48.2652 | 0.56079 | 634.2109 | 95.5 | 46.701 | 2.1249 | 2403.1331 | 46.0307 | 2.7953 | 3161.2427
Oldham | OLDMTX-DCSYS04 | 615 | 34 | 18.0882 | 985.8088 | 90.7451 | 36.6195 | 36.1989 | 0.4206 | 475.6582 | 95.5 | 35.0258 | 1.5937 | 1802.3499 | 34.523 | 2.0965 | 2370.932
Oldham | OLDMTX-DCSYS05 | 637 | 44 | 14.4773 | 789.0114 | 88.5162 | 38.7033 | 37.4938 | 1.2094 | 1367.7764 | 95 | 36.4523 | 2.2509 | 2545.6197 | 35.758 | 2.9453 | 3330.8486
Oldham | OLDMTX-DCSYS06 | 652 | 44 | 14.8182 | 807.5909 | 88.5162 | 39.6146 | 38.3767 | 1.2379 | 1399.9846 | 95 | 37.3107 | 2.3039 | 2605.5637 | 36.6 | 3.0146 | 3409.2831 |  | Site Name | Number of Rectifiers | kWh Saving | NetSure (With ECO) Financial Saving | kWh Saving | eSure (no ECO) Financial Saving | kWh Saving | eSure (with ECO) Financial Saving
Rotherham | PEARM | 401 | 36 | 11.1389 | 607.0694 | 88.5162 | 24.3642 | 23.6029 | 0.76136 | 861.0335 | 93 | 23.3843 | 0.9799 | 1108.1895 | 22.5101 | 1.8541 | 2096.8137 |  | Acton | 180 | 2.3266 | 2631.2254 | 6.9137 | 7818.8684 | 11.003 | 12443.505
Rotherham | PEBRM | 437 | 36 | 12.1389 | 661.5694 | 88.5162 | 26.5515 | 25.7218 | 0.82971 | 938.3332 | 93 | 25.4837 | 1.0679 | 1207.6778 | 24.531 | 2.0205 | 2285.0563 |  | Crawley | 180 | 4.8976 | 5538.7754 | 8.048 | 9101.5821 | 11.2196 | 12688.4263
Rotherham | PECRM | 533 | 36 | 14.8056 | 806.9028 | 88.5162 | 32.3844 | 31.3724 | 1.012 | 1144.4659 | 95 | 30.5009 | 1.8834 | 2130.0083 | 29.92 | 2.4644 | 2787.0366 |  | Edinburgh | 180 | 0.48256 | 545.7322 | 7.9469 | 8987.2511 | 9.813 | 11097.6308
Rotherham | PEDRM | 256 | 36 | 7.1111 | 387.5556 | 82.0732 | 16.4531 | 15.0682 | 1.385 | 1566.3003 | 91 | 15.2077 | 1.2455 | 1408.5149 | 14.3706 | 2.0826 | 2355.2273 |  | Esher | 144 | 5.2864 | 5978.5302 | 5.7775 | 6533.8608 | 9.4366 | 10672.0295
Rotherham | PEERM | 212 | 36 | 5.8889 | 320.9444 | 82.0732 | 13.6253 | 12.4783 | 1.1469 | 1297.0924 | #N/A | #N/A | #N/A | #N/A | 11.9006 | 1.7246 | 1950.4226 |  | Gloucester | 180 | 1.518 | 1716.7374 | 7.5062 | 8488.8745 | 9.2216 | 10428.8336
Southampton | PEASN | 368 | 36 | 10.2222 | 557.1111 | 82.0732 | 23.6514 | 21.6605 | 1.9909 | 2251.5567 | 93 | 21.4599 | 2.1915 | 2478.3732 | 20.6577 | 2.9937 | 3385.6392 |  | Kings Cross | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Southampton | PEBSN | 544 | 36 | 15.1111 | 823.5556 | 88.5162 | 33.0527 | 32.0198 | 1.0329 | 1168.0853 | 95 | 31.1304 | 1.9223 | 2173.9672 | 30.5374 | 2.5153 | 2844.5552 |  | Southampton | 144 | 5.8279 | 6590.8776 | 7.9093 | 8944.7152 | 10.5939 | 11980.8515
Southampton | PECSN | 491 | 36 | 13.6389 | 743.3194 | 88.5162 | 29.8325 | 28.9003 | 0.93224 | 1054.2829 | 95 | 28.0975 | 1.735 | 1962.1653 | 27.5623 | 2.2702 | 2567.4202 |  | Swanley | 180 | 4.9405 | 5587.3404 | 6.8628 | 7761.2041 | 10.5295 | 11908.0017
Southampton | PEESN | 346 | 36 | 9.6111 | 523.8056 | 82.0732 | 22.2375 | 20.3656 | 1.8719 | 2116.9527 | 93 | 20.177 | 2.0605 | 2330.2096 | 19.4227 | 2.8147 | 3183.2369 |  | Totals | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Swanley | PEASY | 538 | 36 | 14.9444 | 814.4722 | 88.5162 | 32.6882 | 31.6667 | 1.0215 | 1155.202 | 95 | 30.7871 | 1.9011 | 2149.9897 | 30.2006 | 2.4875 | 2813.1814
Swanley | PEBSY | 498 | 36 | 13.8333 | 753.9167 | 88.5162 | 30.2578 | 29.3123 | 0.94553 | 1069.3134 | 95 | 28.4981 | 1.7598 | 1990.1391 | 27.9552 | 2.3026 | 2604.0229
Swanley | PECSY | 384 | 36 | 10.6667 | 581.3333 | 88.5162 | 23.3313 | 22.6022 | 0.72908 | 824.5308 | 93 | 22.393 | 0.93836 | 1061.2089 | 21.5558 | 1.7755 | 2007.9213
Swanley | PEDSY | 298 | 36 | 8.2778 | 451.1389 | 82.0732 | 19.1525 | 17.5403 | 1.6122 | 1823.2714 | 91 | 17.7027 | 1.4498 | 1639.5994 | 16.7282 | 2.4243 | 2741.6318 |  | Completed under MTX FY13/14
Swanley | PEESY | 333 | 30 | 11.1 | 604.95 | 88.5162 | 20.2326 | 19.6004 | 0.63225 | 715.0228 | 93 | 19.4189 | 0.81374 | 920.2671 | 18.693 | 1.5397 | 1741.2443
Bristol | PEFBL | 476 | 36 | 13.2222 | 720.6111 | 88.5162 | 28.9211 | 28.0174 | 0.90376 | 1022.0746 |  |  |  |  | 26.7203 | 2.2009 | 2488.9858 |  | Site Name | Number of Rectifiers | NetSure (With ECO) Financial Saving | eSure (no ECO) Financial Saving | eSure (with ECO) Financial Saving | Saving with ECO only on eSure
Bristol | PEHBL | 329 | 36 | 9.1389 | 498.0694 | 82.0732 | 21.1449 | 19.3649 | 1.7799 | 2012.9406 |  |  |  |  | 18.4684 | 2.6764 | 3026.8351 |  | Oldham | 254 | 5196.3246 | 14626.7758 | 18845.3781 | 4218.6022
Cardiff | PECCF | 352 | 36 | 9.7778 | 532.8889 | 82.0732 | 22.6231 | 20.7187 | 1.9044 | 2153.6629 |  |  |  |  | 19.7595 | 2.8636 | 3238.4375 |  | Rotherham | 180 | 5807.2253 | #N/A | 11474.5564 | #N/A
Cardiff | PEDCF | 165 | 18 | 9.1667 | 499.5833 | 82.0732 | 10.6046 | 9.7119 | 0.89267 | 1009.5295 |  |  |  |  | 9.2623 | 1.3423 | 1518.0176 |  |  | Totals | 11003.5499 | #N/A | 30319.9345 | #N/A
Cardiff | PEECF | 210 | 18 | 11.6667 | 635.8333 | 88.5162 | 12.7593 | 12.3606 | 0.39872 | 450.9153 |  |  |  |  | 11.7884 | 0.97097 | 1098.082
Carlisle | PEACE | 400 | 36 | 11.1111 | 605.5556 | 88.5162 | 24.3035 | 23.544 | 0.75946 | 858.8863 |  |  |  |  | 22.454 | 1.8495 | 2091.5847
Carlisle | PEBCE | 444 | 36 | 12.3333 | 672.1667 | 88.5162 | 26.9768 | 26.1338 | 0.843 | 953.3637 |  |  |  |  | 24.9239 | 2.0529 | 2321.659
Croydon | PEFCN | 313 | 36 | 8.6944 | 473.8472 | 82.0732 | 20.1165 | 18.4232 | 1.6934 | 1915.0468 |  |  |  |  | 17.5703 | 2.5463 | 2879.6334
Croydon | PEGCN | 387 | 36 | 10.75 | 585.875 | 88.5162 | 23.5136 | 22.7788 | 0.73478 | 830.9725 |  |  |  |  | 21.7242 | 1.7894 | 2023.6082
Glasgow TXO | PEJGW | 87 | 9 | 9.6667 | 526.8333 | 93 | 5.0734 | 5.1208 | -0.047415 | -53.6224 |  |  |  |  | 4.8837 | 0.18966 | 214.4895
Glasgow TXO | PEKGW | 85 | 9 | 9.4444 | 514.7222 | 91 | 5.0494 | 5.0031 | 0.046325 | 52.3897 |  |  |  |  | 4.7715 | 0.27795 | 314.3381
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF!
Leicester | PEFLR | 626 | 36 | 17.3889 | 947.6944 | 90.7451 | 37.2745 | 36.8464 | 0.42812 | 484.1659 |  |  |  |  | 35.1405 | 2.134 | 2413.3389
Leicester | PEGLR | 520 | 36 | 14.4444 | 787.2222 | 88.5162 | 31.5945 | 30.6072 | 0.9873 | 1116.5521 |  |  |  |  | 29.1902 | 2.4043 | 2719.0601
Newbury | PEGNY | 366 | 36 | 10.1667 | 554.0833 | 82.0732 | 23.5229 | 21.5428 | 1.9801 | 2239.3199 |  |  |  |  | 20.5454 | 2.9774 | 3367.239
Newbury | PEHNY | 314 | 36 | 8.7222 | 475.3611 | 82.0732 | 20.1808 | 18.482 | 1.6988 | 1921.1652 |  |  |  |  | 17.6264 | 2.5544 | 2888.8335
Newcastle | PEENE | 306 | 36 | 8.5 | 463.25 | 82.0732 | 19.6666 | 18.0112 | 1.6555 | 1872.2183 |  |  |  |  | 17.1773 | 2.4893 | 2815.2326
Newcastle | PEFNE | 359 | 36 | 9.9722 | 543.4861 | 82.0732 | 23.073 | 21.1307 | 1.9422 | 2196.4914 |  |  |  |  | 20.1525 | 2.9205 | 3302.8383
Newcastle | PEGNE | 151 | 18 | 8.3889 | 457.1944 | 82.0732 | 9.7048 | 8.8879 | 0.81692 | 923.8724 |  |  |  |  | 8.4764 | 1.2284 | 1389.2161
Oxford | PECOD | 236 | 36 | 6.5556 | 357.2778 | 82.0732 | 15.1677 | 13.891 | 1.2768 | 1443.9331 |  |  |  |  | 13.2479 | 1.9199 | 2171.2252
Oxford | PEFOD | 138 | 30 | 4.6 | 250.7 | 74.9132 | 9.4078 | 8.1227 | 1.2851 | 1453.3381 |  |  |  |  | 7.7466 | 1.6611 | 1878.6191
Stafford | PEESD | 394 | 36 | 10.9444 | 596.4722 | 88.5162 | 23.9389 | 23.1908 | 0.74807 | 846.003 |  |  |  |  | 22.1172 | 1.8217 | 2060.2109
Stafford | PEGSD | 417 | 36 | 11.5833 | 631.2917 | 88.5162 | 25.3364 | 24.5446 | 0.79174 | 895.3889 |  |  |  |  | 23.4083 | 1.9281 | 2180.477
Warrington TXO | PELWN | 209 | 18 | 11.6111 | 632.8056 | 88.5162 | 12.6986 | 12.3017 | 0.39682 | 448.7681 |  |  |  |  | 11.7322 | 0.96634 | 1092.853
Warrington TXO | PEMWN | 156 | 18 | 8.6667 | 472.3333 | 82.0732 | 10.0261 | 9.1822 | 0.84397 | 954.4642 |  |  |  |  | 8.7571 | 1.2691 | 1435.2166
Warrington TXO | PENWN | 361 | 18 | 20.0556 | 1093.0278 | 90.7451 | 21.4953 | 21.2485 | 0.24689 | 279.2075 |  |  |  |  | 20.2647 | 1.2306 | 1391.7178
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | #REF!
[7 empty] | #REF! | #REF! | #REF! | #REF!
[7 empty] | #REF! | #REF! |  | #REF!
| Plant Name | Load (A) | Physical Rectifier Count | Load per Rectifier (A) | Power Output Per Rectifier (W) | NetSure Rectifier Effiency (%) | Total Load on Building (kW) | eSure (with ECO) Theoretical Best (kW) | eSure Delta (kW) - With ECO | eSure (With ECO) Financial Saving
Basingstoke | PEABE | 816 | 36 | 22.6667 | 1235.3333 | 96 | 46.2509 | 45.8062 | 0.44472 | 502.941 |  | Iout(A) | Pout (W) | Effiency (%)
Basingstoke | PEBBE | 840 | 36 | 23.3333 | 1271.6667 | 96 | 47.6112 | 47.1534 | 0.4578 | 517.7333 |  | 6.4 | 348.16 | 91
Basingstoke | PECBE | 809 | 36 | 22.4722 | 1224.7361 | 96 | 45.8541 | 45.4132 | 0.44091 | 498.6265 |  | 9.6 | 522.24 | 93
Basingstoke | PEEBE | 869 | 36 | 24.1389 | 1315.5694 | 96 | 49.2549 | 48.7813 | 0.4736 | 535.6075 |  | 12.8 | 696.32 | 95
Basingstoke | PEFBE | 847 | 36 | 23.5278 | 1282.2639 | 96 | 48.008 | 47.5463 | 0.46161 | 522.0478 |  | 16 | 870.4 | 95.5
Basingstoke | PEGBE | 878 | 36 | 24.3889 | 1329.1944 | 96 | 49.765 | 49.2865 | 0.47851 | 541.1546 |  | 19.2 | 1044.48 | 96
Basingstoke | PEHBE | 872 | 36 | 24.2222 | 1320.1111 | 96 | 49.425 | 48.9497 | 0.47524 | 537.4565 |  | 25.6 | 1392.64 | 97
Basingstoke | PEIBE | 907 | 36 | 25.1944 | 1373.0972 | 96 | 51.4088 | 50.9144 | 0.49432 | 559.0287 |  | 32 | 1740.8 | 97
Gravelly Hill | BMGMTX-DCSYS01 | 766 | 44 | 17.4091 | 948.7955 | 95.5 | 43.6256 | 42.9994 | 0.6262 | 708.1853 |  | 38.4 | 2088.96 | 97
Gravelly Hill | BMGMTX-DCSYS02 | 785 | 44 | 17.8409 | 972.3295 | 95.5 | 44.7077 | 44.066 | 0.64174 | 725.7512 |  | 44.8 | 2437.12 | 96.2
Gravelly Hill | PECGL | 858 | 36 | 23.8333 | 1298.9167 | 96 | 48.6314 | 48.1638 | 0.46761 | 528.8276 |  | 51.2 | 2785.28 | 96
Gravelly Hill | BMGMTX-DCSYS04 | 797 | 44 | 18.1136 | 987.1932 | 95.5 | 45.3911 | 44.7396 | 0.65155 | 736.8455 |  | 57.6 | 3133.44 | 95.5
Gravelly Hill | BMGMTX-DCSYS05 | 799 | 44 | 18.1591 | 989.6705 | 95.5 | 45.505 | 44.8519 | 0.65318 | 738.6945 |  | 64 | 3481.6 | 95
Gravelly Hill | PEFGL | 844 | 36 | 23.4444 | 1277.7222 | 96 | 47.8379 | 47.3779 | 0.45998 | 520.1987
Leyland | LLDMTX-DCSYS01 | 901 | 44 | 20.4773 | 1116.0114 | 96 | 51.0687 | 50.5776 | 0.49104 | 555.3306
Leyland | LLDMTX-DCSYS02 | 810 | 44 | 18.4091 | 1003.2955 | 95.5 | 46.1315 | 45.4693 | 0.66217 | 748.8643
Leyland | LLDMTX-DCSYS03 | 929 | 44 | 21.1136 | 1150.6932 | 96 | 52.6557 | 52.1494 | 0.50631 | 572.5884
Leyland | LLDMTX-DCSYS04 | 859 | 44 | 19.5227 | 1063.9886 | 96 | 48.6881 | 48.22 | 0.46816 | 529.444
Leyland | LLDMTX-DCSYS05 | 910 | 44 | 20.6818 | 1127.1591 | 96 | 51.5788 | 51.0829 | 0.49595 | 560.8778
Leyland | LLDMTX-DCSYS06 | 898 | 44 | 20.4091 | 1112.2955 | 96 | 50.8986 | 50.4092 | 0.48941 | 553.4816
Milton Keynes | PEAMS | 1046 | 42 | 24.9048 | 1357.3095 | 96 | 59.2873 | 58.7172 | 0.57007 | 644.7013
Milton Keynes | PEBMS | 988 | 42 | 23.5238 | 1282.0476 | 96 | 55.9998 | 55.4614 | 0.53846 | 608.953
Milton Keynes | PECMS | 960 | 42 | 22.8571 | 1245.7143 | 96 | 54.4128 | 53.8896 | 0.5232 | 591.6953
Milton Keynes | PEDMS | 1131 | 42 | 26.9286 | 1467.6071 | 97 | 63.4887 | 63.4887 | 0 | 0
Milton Keynes | PEEMS | 1051 | 42 | 25.0238 | 1363.7976 | 96 | 59.5707 | 58.9979 | 0.57279 | 647.783
Milton Keynes | PEFMS | 1045 | 42 | 24.881 | 1356.0119 | 96 | 59.2306 | 58.6611 | 0.56952 | 644.0849
14289.7485

## Title Page (hidden)
MTX Space and Power Utilisation July 2017
Leigh Peake, MTX Infrastructure Team

## Info (hidden)
MTX Site Information
The MTX sites are split into the following categories-
Core MTX Sites contain Core Network elements (switching, messaging and IN) RAN Capability and Transmission equipment
x9 strategic sites for new Core deployment
x5 non-strategic sites closed to new Core deployment
Network Aggregation Sites
x12 sites that generally only contain RAN Capability and Transmission equipment
x2 sites that only contain Transmission equipment
Canal House Computer Room at XNY has been included in the report as it is under Networks control

## DC_9 (hidden)
Strategic Core MTX Sites - Power Breakdown
Power capability is defined as the maximum power available to technology given each building's infrastructure capability
The remaining power capability at XMS is reserved for Virtulisation and is not currently deployed
STRATEGIC SITES FOR NEW CORE DEPLOYMENT
* - CHE SITEC
Power (kW)

## CHE Pwr (hidden)
Derived AC expansion and deployed capability is subject to DC power availability at each site
The reserved and forecast figures at XBE, XMS and XLD are for Virtulisation use
IC13GL, IC14GL, IC12LD and IC13LD are TSi inverter systems for Voicemail use
CHE Sites - Power Breakdown

## Non-CHE Pwr (hidden)
Power (kW)
Strategic Sites (Non- CHE) - Plant Usage
AC expansion and deployed capability is subject to DC power availability at each site
HLR and DSC cabs at XCY and XGR are installed and included in the forecast figures , but not due to be powered on until 2018
IC5AN is reserved for security cab use

## Strat 12Mth DC (hidden)
Strategic Core MTX Sites - 12 Month Power Usage
Power usage figures on AC plants are included in the DC figures as AC power is derived from the DC plants
XGL and XLD values include TSi inverter figures that are powered by raw mains
There has been an overall decrease in power usage of 113kW across Strategic Core MTX sites. However, the forecast and reserved figures predict an increase of 461kW, resulting in an increase of 288kW year on year
Power decreases - The decreases at XBE, XGL, XMS, and XLD are due to a combination of the powering down of MCA, ACF, CLS and SSM cabs and CHE and Vosnet cab equipment
Forecast and Reserved figures - At XAN, there is 20kW reserved to support a new security cab suite
- Virtulisation requirements account for the reserved and forecast figures at XBE, XLD and XMS

## StratSpace (hidden)
Strategic Core MTX Sites - Switchroom Floor Space Usage
At the CHE sites, and at XAN, hot air containment areas are deployed
These areas are to allow for deployment of platforms that have large power requirements and therefore exhaust a considerable amount of hot air. Such equipment includes Voice Mail, VCA, Gi LAN and SPGW platforms
The reserved and forecast spaces at XBE, XLD and XMS are to be used for Virtulisation hardware
The above figures are based on total switchroom floorspace, minus the hot air containment areas at the CHE sites and XAN and caged areas at XAN and XBE
Space has been reserved for new inverter systems at XAN, XCY, XGR, XOM and XRM and for NFV cabs at XBE and XMS
Hot Air Containment
STRATEGIC SITES CLOSED TO NEW CORE DEPLOYMENT

## NS DC (hidden)
Power (kW)
Non- Strategic Core MTX Sites - Power Breakdown
Power capability is defined as the maximum power available to technology given each building's infrastructure capability
At XKS, due to the limitations regarding the power on the 2nd floor, deployment to this floor is restricted
The reserved power at XEH is for Virtulisation use
SITES CLOSED TO NEW CORE DEPLOYMENT
Power (kW)

## NS AC_DC (hidden)
Non- Strategic Core MTX Sites - Plant Usage
Power (kW)
Non- Strategic Core Sites DC Plant Utilisation
Power (kW)
Non- Strategic Core Sites AC Plant Utilisation
AC expansion and deployed capability is subject to DC power availability at each site
The reserved figure at XEH is for Virtulisation use

## NS12 Mth DC (hidden)
Non- Strategic Core MTX Sites - 12 Month Power Usage
Power usage figures on AC plants are included in the DC figures as AC power is derived from the DC plants
There has been a decrease of 22kW in power usage across Non- Strategic Core MTX sites. The forecast and reserved figures predict an increase of 158kW, resulting in a increase of 136kW year on year
Power Decreases - Power downs of RNC, BSC and CBX elements along with the power down and closure of the basement have contibuted to power decrease figures at XKS
Forecast and Reserved Figures - At XSY, the reserved figures include 4kW for CSDB (installed HLR cab not due to be powered on until 2018)
SITES CLOSED TO NEW CORE DEPLOYMENT

## NS Space (hidden)
Non- Strategic Core MTX Sites - Switchroom Floor Space Usage
The XKS floorspace figures exclude the caged area on the 3rd floor
Space has been reserved for new inverter systems at the above sites
At XEH, space has also been reserved for x15 Virtulistaion cabs
Space (m²)
NON- STRATEGIC SITES CLOSED TO NEW CORE DEPLOYMENT

## Bldg Pwr Type A+B (hidden)
Core & Network Aggregation Sites - Power Utilisation

## Bldg Pwr Type A+B (2) (hidden)
Core & Network Aggregation Sites - Power Utilisation

## PUE (hidden)
Power usage effectiveness (PUE) is a measure of how efficiently an MTX uses its power; specifically, how much of the power is actually used by the technology elements in contrast to cooling and other overheads
PUE readings are the average figures taken from the Vodafone Building Management System (BMS)
A PUE value of 1.5 is our current target, the lower the PUE value, the better the energy efficiency of the MTX
The building infrastructure that governs the PUE value is controlled by MITIE
Core MTX Sites - Power Usage Effectiveness (PUE)

## NW Agg Pwr (hidden)
Network Aggregation Sites - Power Breakdown
Canal House Computer Room
Floor Space Usage

## Assumption (hidden)
Assumptions
For both the Space and Power data, removals will only be included once the actual equipment removal is complete
Likewise, increases in Max Technology Load or Deployed AC or DC Capacity will only be included once the power plant is operational
Forecast figures are based on pre-allocated resources, following review via the space and power governance process, for installations or expansion where the details of the requirement are clear. Forecasts are usually only valid for a period of up to 3 months from receipt of the request after which the request must be reviewed again.
Reserved figures are based on resources earmarked for future expansion of specific services or infrastructure to prevent their use for other, unrelated, purposes. This typically applies to resources where no other suitable solution is available to satisfy the future requirement. Reserved resource status should be reviewed on a 6 monthly basis.
For Information
Basingstoke and Kings Cross MTX’s are fitted with 1.25MVA generators but the maximum technology load is still capped at 504kW for XBE (the same as Gravelly Hill which has 1MVA generators installed), and 450kW for XKS, this is due to the additional air conditioning at Kings Cross as a result of the multi-floor arrangement.

## XLD TSI Plant (hidden)
Site Name | Plant Name | Load (A) | Site kW | Forecast (A) |  | Forecast +Current | Remaining Capacity
Leyland | PEALD | 674 | 208.953 | 7 | 5.1275 | 681 | 466 | 40.35% | 57.8%
Leyland | PEBLD | 583 |  | 7 |  | 590 | 534 | 46.23%
Leyland | PECLD | 606 |  | 7 |  | 613 | 537 | 46.49%
Leyland | PEDLD | 589 |  | 7 |  | 596 | 516 | 44.68%
Leyland | PEELD | 722 |  | 7 |  | 729 | 431 | 37.32%
Leyland | PEFLD | 596 |  | 0 |  | 596 | 577 | 49.96%
MTX | Name | Type | Total Number of Inverters | Redundant inverters | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | System Load May (A) | System Load May (kW) | Total Load on DC power plants (kW) | Forecast Load (A) | Forecast Load (kW) | Load per inverter
XLD | IC7LD | RDI | 18 | 5 | 39 | 169 | 3 | 67 | 15 | 16.35 | 0 | 0 | 16.6667
XLD | IC8LD | RDI | 18 | 5 | 39 | 169 | 3 | 37 | 8 | 8.72 | 0 | 0 | 8.8889
XLD | IC9LD | RDI | 18 | 5 | 39 | 169 | 3 | 30 | 6 | 6.54 | 8 | 1.84 | 6.6667
XLD | IC10LD | RDI | 8 | 3 | 15 | 65 | 27 | 2 | 0 | 0 | 0 | 0 | 0
| IC7LD | IC8LD | IC9LD | IC10LD | Inverter Load on Plant | Revised Plant Load | Number of ccts on plant | TSI Load | Plant Total with TSI | Delta
PEALD | 4 | 3 | 4 |  | 120 | 554 | 9 | 104.94 | 658.94 | -15.06
PEBLD | 3 | 3 | 3 |  | 96.6667 | 486.3333 | 9 | 104.94 | 591.2733 | 8.2733
PECLD | 3 | 4 | 3 |  | 105.5556 | 500.4444 | 9 | 104.94 | 605.3844 | -0.61556
PEDLD | 4 | 4 | 4 |  | 128.8889 | 460.1111 | 8 | 93.28 | 553.3911 | -35.6089
PEELD | 4 | 4 | 4 |  | 128.8889 | 593.1111 | 8 | 93.28 | 686.3911 | -35.6089
PEFLD |  |  |  |  | 0 | 596 | 9 | 104.94 | 700.94 | 104.94
| Number of Modules | Total Load (kW) | Load Per Module (A)
IC30aLD | 26 | 15.5 | 11.66 |  | Max load per module | 11.66
IC30bLD | 26 | 15.5 | 11.66
| IC30aLD | IC30bLD
PEALD |  | 9
PEBLD | 9
PECLD | 9
PEDLD | 8
PEELD |  | 8
PEFLD |  | 9
| 26 | 26

## XGL TSI Plant (hidden)
Site Name | Plant Name | Load (A) | Site kW | Forecast (A) |  | Forecast +Current | Remaining Capacity
Gravelly Hill | PEAGL | 756 | 274.571 | 7 | 9.7055 | 763 | 392 | 33.94% | 73.84%
Gravelly Hill | PEBGL | 814 |  | 49 |  | 863 | 292 | 25.28%
Gravelly Hill | PECGL | 903 |  | 7 |  | 910 | 245 | 21.21%
Gravelly Hill | PEDGL | 869 |  | 49 |  | 918 | 237 | 20.52%
Gravelly Hill | PEEGL | 861 |  | 0 |  | 861 | 294 | 25.45%
Gravelly Hill | PEFGL | 835 |  | 7 |  | 842 | 313 | 27.1%
MTX | Name | Type | Total Number of Inverters | Redundant inverters | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | System Load May (A) | System Load May (kW) | Total Load on DC power plants (kW) | Forecast Load (A) | Forecast Load (kW) | Load per inverter
XGL | IC9GL | RDI | 18 | 5 | 39 | 169 | 3 | 66 | 15 | 16.35 |  |  | 16.6667
XGL | IC10GL | RDI | 18 | 5 | 39 | 169 | 3 | 71 | 16 | 17.44 |  |  | 17.7778
XGL | IC11GL | RDI | 18 | 5 | 39 | 169 | 3 | 64 | 14 | 15.26 |  |  | 15.5556
XGL | IC12GL | RDI | 9 | 2 | 21 | 91 | 21 | 31 | 7 | 7.63 |  |  | 15.5556
| IC9GL | IC10GL | IC11GL | IC12GL | Inverter Load on Plant | Revised Plant Load | Number of ccts on plant | TSI Load | Plant Total with TSI | Delta
PEAGL | 4 | 4 | 4 | 2 | 231.1111 | 524.8889 | 20 | 254.4 | 779.2889 | 23.2889
PEBGL | 3 | 3 | 3 | 1 | 165.5556 | 648.4444 | 14 | 178.08 | 826.5244 | 12.5244
PECGL | 3 | 3 | 3 | 2 | 181.1111 | 721.8889 | 14 | 178.08 | 899.9689 | -3.0311
PEDGL | 4 | 4 | 4 | 2 | 231.1111 | 637.8889 | 14 | 178.08 | 815.9689 | -53.0311
PEEGL |  |  |  |  | 0 | 861 | 7 | 89.04 | 950.04 | 89.04
PEFGL | 4 | 4 | 4 | 2 | 231.1111 | 603.8889 | 15 | 190.8 | 794.6889 | -40.3111
| Number of Modules | Total Load (kW) | Load Per Module (A)
IC30aGL | 21 | 13.5 | 12.72 |  | Max load per module | 12.72
IC30bGL | 21 | 13.5 | 12.72
IC31aGL | 21 | 13.5 | 12.72
IC31bGL | 21 | 13.5 | 12.72
| IC30aGL | IC30bGL | IC31aGL | IC31bGL
PEAGL |  | 10 |  | 10
PEBGL | 7 |  | 7
PECGL | 7 |  | 7
PEDGL | 7 |  | 7
PEEGL |  | 2 |  | 5
PEFGL |  | 9 |  | 6
| 21 | 21 | 21 | 21

## XMS TSI Plant (hidden)
Site Name | Plant Name | Load (A) | Site kW | Forecast (A) |  | Forecast +Current | Remaining Capacity
Milton Keynes | PEAMS | 787
Milton Keynes | PEBMS | 765
Milton Keynes | PECMS | 765
Milton Keynes | PEDMS | 663
Milton Keynes | PEEMS | 777
Milton Keynes | PEFMS | 850
MTX | Name | Type | Total Number of Inverters | Redundant inverters | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | System Load May (A) | System Load May (kW) | Total Load on DC power plants (kW) | Forecast Load (A) | Forecast Load (kW) | Load per inverter
XMS | IC6MS | RDI | 18 | 4 | 42 | 182 | 0 | 85 | 19 | 20.71 |  |  | 21.1111
XMS | IC7MS | RDI | 18 | 4 | 42 | 182 | 0 | 57 | 13 | 14.17 |  |  | 14.4444
XMS | IC8MS | RDI | 18 | 4 | 42 | 182 | 0 | 47 | 10 | 10.9 |  |  | 11.1111
#DIV/0!
| IC6MS | IC7MS | IC8MS |  | Inverter Load on Plant | Revised Plant Load | Number of ccts on plant | TSI Load | Plant Total with TSI | Delta
PEAMS | 3 | 3 | 3 |  | 140 | 647 | 13 | 206.7 | 853.7 | 66.7
PEBMS | 3 | 3 | 3 |  | 140 | 625 | 11 | 174.9 | 799.9 | 34.9
PECMS | 3 | 3 | 3 |  | 140 | 625 | 12 | 190.8 | 815.8 | 50.8
PEDMS | 3 | 3 | 3 |  | 140 | 523 | 13 | 206.7 | 729.7 | 66.7
PEEMS | 3 | 3 | 3 |  | 140 | 637 | 12 | 190.8 | 827.8 | 50.8
PEFMS | 3 | 3 | 3 |  | 140 | 710 | 11 | 174.9 | 884.9 | 34.9
| Number of Modules | Total Load (kW) | Load Per Module (A)
IC30aMS | 14 | 10 | 14.84 |  | Max load per module | 15.9
IC30bMS | 14 | 10 | 14.84
IC31aMS | 22 | 17.5 | 15.9
IC31bMS | 22 | 17.5 | 15.9

## XBE TSI Plant (hidden)
Site Name | Plant Name | Load (A)
Basingstoke | PEABE | 766
Basingstoke | PEBBE | 815
Basingstoke | PECBE | 732
Basingstoke | PEEBE | 809
Basingstoke | PEFBE | 848
Basingstoke | PEGBE | 321
Basingstoke | PEHBE | 815
Basingstoke | PEIBE | 797
MTX | Name | Type | Total Number of Inverters | Redundant inverters | Deployed Capacity (kW) | Deployed Capacity (A) | Expansion Capability (kW) | System Load May (A) | System Load May (kW) | Total Load on DC power plants (kW) | Forecast Load (A) | Forecast Load (kW) | Load per inverter
XBE | IC10BE | RDI | 18 | 4 | 42 | 182 | 0 | 108 | 24 | 26.16 |  |  | 26.6667
XBE | IC11BE | RDI | 18 | 4 | 42 | 182 | 0 | 110 | 25 | 27.25 |  |  | 27.7778
XBE | IC12BE | RDI | 18 | 4 | 42 | 182 | 0 | 86 | 19 | 20.71 |  |  | 21.1111
XBE | IC13BE | RDI | 18 | 4 | 42 | 182 | 0 | 46 | 10 | 10.9 |  |  | 11.1111
XBE | IC14BE | RDI | 18 | 4 | 42 | 182 | 0 | 33 | 7 | 7.63 |  |  | 7.7778
| IC10BE | IC11BE | IC12BE | IC13BE | IC14BE | Inverter Load on Plant | Revised Plant Load | Number of ccts on plant | TSI Load | Plant Total with TSI | Delta
PEABE | 3 | 2 | 3 | 3 | 3 | 255.5556 | 510.4444 | 10 | 190.8 | 701.2444 | -64.7556
PEBBE | 3 | 3 | 2 | 3 | 3 | 262.2222 | 552.7778 | 10 | 190.8 | 743.5778 | -71.4222
PECBE | 3 | 2 | 3 | 3 |  | 232.2222 | 499.7778 | 20 | 381.6 | 881.3778 | 149.3778
PEEBE | 3 | 3 | 2 | 3 | 3 | 262.2222 | 546.7778 | 20 | 381.6 | 928.3778 | 119.3778
PEFBE | 3 | 3 | 2 | 2 | 3 | 251.1111 | 596.8889 | 20 | 381.6 | 978.4889 | 130.4889
PEGBE | [5 empty] | 0 | 321 | 20 | 381.6 | 702.6 | 381.6
PEHBE | 3 | 3 | 3 | 2 | 3 | 272.2222 | 542.7778 | 10 | 190.8 | 733.5778 | -81.4222
PEIBE |  | 2 | 3 | 2 | 3 | 164.4444 | 632.5556 | 10 | 190.8 | 823.3556 | 26.3556
| Number of Modules | Total Load (kW) | Load Per Module (A)
IC30aBE | 30 | 28 | 19.08 |  | Max load per module | 19.08
IC30bBE | 30 | 28 | 19.08
IC31aBE | 30 | 28 | 19.08
IC31bBE | 30 | 28 | 19.08
| IC30aBE | IC30bBE | IC31aBe | IC31bBE
PEABE |  |  |  | 10
PEBBE |  |  |  | 10
PECBE | 10 |  |  | 10
PEEBE | 10 |  | 10
PEFBE | 10 |  | 10
PEGBE |  | 10 | 10
PEHBE |  | 10
PEIBE |  | 10
| 30 | 30 | 30 | 30

## PUE Values (hidden)
2017
Site Name | Current Usage (kW) | Building Load (kW) | Building Load Correction (from BMS) | PUE |  | Jan PUE | Feb PUE | Mar PUE | Apr PUE | May PUE | June PUE | July PUE | Aug PUE | Sep PUE
XBE | 372.671 | 583.8 | 33 | 1.478 | Was no correction | 1.38 | 1.43 | 1.47 | 1.49 | 1.54 | 1.57 | 1.58 | 1.56 | 1.55
XGL | #REF! | 564 | 0 | #REF! | Correction was 5 | 1.37 | 1.40 | 1.43 | 1.43 | 1.52 | 1.53 | 1.51 | 1.51 | 1.48
XLD | #REF! | 445.5 | 5 | #REF! |  | 1.43 | 1.43 | 1.46 | 1.46 | 1.5 | 1.54 | 1.52 | 1.5 | 1.49
XMS | 367.766 | 402.6 | 0 | 1.0947 |  | 1.29 | 1.34 | 1.37 | 1.36 | 1.36 | 1.44 | 1.42 | 1.42 | 1.42
XAN | 173.528 | 240 | 10 | 1.3254 | Was no correction | 1.57 | 1.63 | 1.67 | 1.68 | 1.73 | 1.88 | 2.06 | 1.77 | 1.74
XCY | 126.44 | 199.3 | 5 | 1.5367 | Was no correction | 1.32 | 1.37 | 1.41 | 1.43 | 1.43 | 1.44 | 1.44 | 1.44 | 1.45
XGR | 260.183 | 254 | 0 | 0.97624 |  | 1.35 | 1.38 | 1.40 | 1.40 | 1.45 | 1.48 | 1.5 | 1.32 | 1.43
XOM | 293.21 | 419.5 | 5 | 1.4137 | Correction was 5 | 1.39 | 1.33 | 1.43 | 1.43 | 1.51 | 1.54 | 1.49 | 1.5 | 1.55
XRM | 100.2255 | 309.9 | 10 | 2.9923 |  | 1.42 | 1.36 | 1.50 | 1.48 | 1.47 | 1.5 | 1.5 | 1.32 | 1.26
XEH | 285.6345 | 317.5 | 15 | 1.059 | Correction was 40 | 1.29 | 1.28 | 1.33 | 1.36 | 1.42 | 1.44 | 1.4 | 1.21 | 1.28
XER | 83.0035 | 224.5 | 10 | 2.5842 | Correction was 5 | 2.04 | 1.84 | 1.71 | 1.95 | 2.03 | 1.83 | 1.89 | 1.89 | 1.81
XKS | 127.4755 | 399 | 0 | 3.13 |  | 1.92 | 1.92 | 1.94 | 1.98 | 1.97 | 1.97 | 1.99 | 1.99 | 1.97
XSN | 95.3205 | 224.2 | 5 | 2.2996 | Same | 1.74 | 1.74 | 1.80 | 1.77 | 1.8 | 1.85 | 1.81 | 1.83 | 1.81
XSY | 111.7795 | 225.9 | 5 | 1.9762 | Same | 1.36 | 1.38 | 1.43 | 1.43 | 1.46 | 1.48 | 1.49 | 1.47 | 1.46
Updated correction figs as of 24/07/13
Air flow mgmt completed
Free air cooling completed
GRAPHING FIGS
Site Name | July 16 PUE | July 17 PUE
XBE | 1.55 | 1.58
XGL | 1.48 | 1.51 | [7 empty] | For latest PUE figs, from Sept 2017, see \team\Team Presentations\PUE Presentations 2017
XLD | 1.53 | 1.52
XMS | 1.4 | 1.42
XAN | 1.73 | 2.06
XCY | 1.56 | 1.44
XGR | 1.49 | 1.5
XOM | 1.54 | 1.49
XRM | 1.52 | 1.5
Site Name | July 16 PUE | July 17 PUE
XEH | 1.46 | 1.4
XER | 1.76 | 1.89
XKS | 2.02 | 1.99
XSN | 1.74 | 1.81
XSY | 1.49 | 1.49
[18 empty] | Building load | A | KW
[6 empty] | 2016 | [11 empty] | Side A |  | 0
Site Name | Current Usage (kW) | Building Load (kW) | Building Load Correction (from BMS) | PUE |  | Jan PUE | Feb PUE | Mar PUE | Apr PUE | May PUE | Jun PUE | Jul PUE | Aug PUE | Sep PUE | Oct PUE | Nov PUE | Dec PUE | Side B |  | 0
XBE | 0 | 583.8 | 33 | #DIV/0! | Was no correction | 1.42 | 1.42 | 1.38 | 1.43 | 1.46 | 1.52 | 1.55 | 1.54 | 1.55 | 1.51 | 1.46 | 1.43 | Total | 0 | 0
XGL | #REF! | 564 | 0 | #REF! | Correction was 5 | 1.37 | 1.38 | 1.32 | 1.4 | 1.46 | 1.48 | 1.48 | 1.5 | 1.48 | 1.44 | 1.38 | 1.4
XLD | #REF! | 445.5 | 5 | #REF! |  | 1.41 | 1.41 | 1.3 | 1.46 | 1.49 | 1.54 | 1.53 | 1.51 | 1.5 | 1.47 | 1.4 | 1.46
XMS | #REF! | 402.6 | 0 | #REF! |  | 1.4 | 1.29 | 1.25 | 1.36 | 1.37 | 1.37 | 1.4 | 1.4 | 1.39 | 1.38 | 1.31 | 1.33
XAN | 127.4755 | 240 | 10 | 1.8043 | Was no correction | 1.55 | 1.6 | 1.58 | 1.62 | 1.67 | 1.72 | 1.73 | 1.73 | 1.73 | 1.69 | 1.63 | 1.62
XCY | 0 | 199.3 | 5 | #DIV/0! | Was no correction | 1.58 | 1.55 | 1.55 | 1.49 | 1.47 | 1.47 | 1.56 | 1.64 | 1.55 | 1.44 | 1.37 | 1.36
XGR | 0 | 254 | 0 | #DIV/0! |  | 1.45 | 1.55 | 1.55 | 1.44 | 1.52 | 1.52 | 1.49 | 1.47 | 1.45 | 1.4 | 1.34 | 1.34
XOM | 0 | 419.5 | 5 | #DIV/0! | Correction was 5 | 1.41 | 1.39 | 1.41 | 1.43 | 1.46 | 1.51 | 1.54 | 1.55 | 1.5 | 1.38 | 1.35 | 1.36
XRM | 20.383 | 309.9 | 10 | 14.7132 |  | 1.45 | 1.46 | 1.47 | 1.47 | 1.54 | 1.55 | 1.52 | 1.62 | 1.51 | 1.44 | 1.37 | 1.45
XEH | 0 | 317.5 | 15 | #DIV/0! | Correction was 40 | 1.3 | 1.28 | 1.28 | 1.31 | 1.26 | 1.43 | 1.46 | 1.45 | 1.45 | 1.36 | 1.51 | 1.35
XER | 293.21 | 224.5 | 10 | 0.73156 | Correction was 5 | 1.93 | 1.77 | 1.74 | 1.74 | 1.98 | 1.86 | 1.76 | 1.87 | 2.12 | 1.74 | 2.03 | 2.03
XKS | 111.7795 | 399 | 0 | 3.5695 |  | 1.92 | 2.02 | 1.95 | 1.93 | 1.96 | 2 | 2.02 | 2.14 | 2.04 | 1.95 | 1.92 | 2.01
XSN | 0 | 224.2 | 5 | #DIV/0! | Same | 1.74 | 1.8 | 1.84 | 1.86 | 1.81 | 1.77 | 1.74 | 1.75 | 1.75 | 1.76 | 1.75 | 1.75
XSY | #REF! | 225.9 | 5 | #REF! | Same | 1.42 | 1.38 | 1.42 | 1.5 | 1.51 | 1.51 | 1.49 | 1.49 | 1.55 | 1.45 | 1.4 | 1.4
2015
Site Name | Current Usage (kW) | Building Load (kW) | Building Load Correction (from BMS) | PUE |  | Jan PUE | Feb PUE | Mar PUE | Apr PUE | May PUE | Jun PUE | Jul PUE | Aug PUE | Sep PUE | Oct PUE | Nov PUE | Dec PUE
XBE | 0 | 583.8 | 33 | #DIV/0! | Was no correction | 1.59 | 1.5 | 1.46 | 1.49 | 1.49 | 1.5 | 1.51 | 1.5 | 1.48 | 1.46 | 1.46 | 1.47
XGL | 339 | 564 | 0 | 1.6637 | Correction was 5 | 1.51 | 1.34 | 1.37 | 1.42 | 1.45 | 1.48 | 1.5 | 1.49 | 1.52 | 1.45 | 1.44 | 1.39
XLD | 275 | 445.5 | 5 | 1.6018 |  | 1.43 | 1.39 | 1.41 | 1.4 | 1.48 | 1.51 | 1.53 | 1.55 | 1.55 | 1.54 | 1.47 | 1.41
XMS | #REF! | 402.6 | 0 | #REF! |  | 1.3 | 1.32 | 1.34 | 1.39 | 1.4 | 1.43 | 1.43 | 1.45 | 1.38 | 1.38 | 1.42 | 1.27
XAN | 0 | 240 | 10 | #DIV/0! | Was no correction | 1.55 | 1.52 | 1.52 | 1.67 | 1.68 | 1.72 | 1.7 | 1.68 | 1.68 | 1.63 | 1.61 | 1.69
XCY | 0 | 199.3 | 5 | #DIV/0! | Was no correction | 1.52 | 1.46 | 1.54 | 1.43 | 1.42 | 1.5 | 1.5 | 1.5 | 1.49 | 1.46 | 1.42 | 1.63
XGR | 0.63056 | 254 | 0 | 402.8171 |  | 1.54 | 1.47 | 1.43 | 1.45 | 1.48 | 1.53 | 1.57 | 1.53 | 1.52 | 1.52 | 1.51 | 1.51
XOM | 37.06 | 419.5 | 5 | 11.1846 | Correction was 5 | 1.62 | 1.62 | 1.61 | 1.56 | 1.58 | 1.58 | 1.57 | 1.57 | 1.51 | 1.49 | 1.49 | 1.42
XRM | 0 | 309.9 | 10 | #DIV/0! |  | 1.6 | 1.46 | 1.38 | 1.42 | 1.43 | 1.47 | 1.51 | 1.5 | 1.56 | 1.59 | 1.54 | 1.48
XEH | 367.766 | 317.5 | 15 | 0.82253 | Correction was 40 | 1.92 | 1.91 | 1.9 | 1.92 | 1.89 | 1.84 | 1.52 | 1.57 | 1.58 | 1.58 | 1.58 | 1.38
XER | 0 | 224.5 | 10 | #DIV/0! | Correction was 5 | 1.6 | 1.59 | 1.67 | 2 | 1.92 | 2 | 2.01 | 2.09 | 1.95 | 1.95 | 2.07 | 2.07
XKS | 0 | 399 | 0 | #DIV/0! |  | 1.9 | 1.9 | 1.91 | 1.93 | 1.94 | 1.99 | 2.06 | 2.07 | 2.07 | 2.07 | 1.94 | 1.97
XSN | 39.567 | 224.2 | 5 | 5.54 | Same | 1.82 | 1.82 | 1.75 | 1.66 | 1.7 | 1.72 | 1.75 | 1.75 | 1.72 | 1.72 | 1.73 | 1.74
XSY | 0 | 225.9 | 5 | #DIV/0! | Same | 1.61 | 1.58 | 1.6 | 1.69 | 1.68 | 1.52 | 1.49 | 1.5 | 1.49 | 1.49 | 1.47 | 1.48
2014
Site Name | Current Usage (kW) | Building Load (kW) | Building Load Correction (from BMS) | PUE |  | Jan PUE | Feb PUE | March PUE | April PUE | May PUE | June PUE | July PUE | Aug PUE | Sep PUE | Oct PUE | Nov PUE | Dec PUE
XBE | 0 | 583.8 | 33 | #DIV/0! | Was no correction | 1.61 | 1.55 | 1.63 | 1.64 | 1.66 | 1.66 | 1.69 | 1.69 | 1.66 | 1.61 | 1.59 | 1.59
XGL | 339 | 564 | 0 | 1.6637 | Correction was 5 | 1.62 | 1.65 | 1.76 | 1.77 | 1.66 | 1.65 | 1.68 | 1.65 | 1.66 | 1.65 | 1.65 | 1.63
XLD | 275 | 445.5 | 5 | 1.6018 |  | 1.61 | 1.57 | 1.74 | 1.73 | 1.65 | 1.72 | 1.77 | 1.79 | 1.8 | 1.78 | 1.66 | 1.45
XMS | #REF! | 402.6 | 0 | #REF! |  | 1.54 | 1.62 | 1.78 | 1.81 | 1.76 | 1.77 | 1.83 | 1.83 | 1.57 | 1.54 | 1.53 | 1.35
XAN | 0 | 240 | 10 | #DIV/0! | Was no correction | 1.73 | 1.71 | 1.71 | 1.76 | 1.76 | 1.74 | 1.72 | 1.72 | 1.74 | 1.73 | 1.64 | 1.59
XCY | 0 | 199.3 | 5 | #DIV/0! | Was no correction | 1.69 | 1.77 | 1.79 | 1.78 | 1.77 | 1.77 | 1.8 | 1.8 | 1.53 | 1.48 | 1.5 | 1.52
XGR | 0.63056 | 254 | 0 | 402.8171 |  | 1.67 | 1.69 | 1.71 | 1.55 | 1.52 | 1.53 | 1.55 | 1.55 | 1.56 | 1.52 | 1.57 | 1.56
XOM | 37.06 | 419.5 | 5 | 11.1846 | Correction was 5 | 1.74 | 1.69 | 1.75 | 1.77 | 1.66 | 1.69 | 1.75 | 1.81 | 1.81 | 1.8 | 1.77 | 1.61
XRM | 0 | 309.9 | 10 | #DIV/0! |  | 1.8 | 1.75 | 1.77 | 1.86 | 1.75 | 1.7 | 1.76 | 1.79 | 1.8 | 1.8 | 1.8 | 1.71
XEH | 367.766 | 317.5 | 15 | 0.82253 | Correction was 40 | 2.04 | 2.05 | 2.01 | 1.97 | 1.99 | 2.05 | 2.03 | 2 | 2 | 1.99 | 2.01 | 1.93
XER | 0 | 224.5 | 10 | #DIV/0! | Correction was 5 | 1.84 | 1.74 | 1.83 | 1.84 | 1.95 | 2.22 | 2.29 | 2.29 | 1.79 | 1.76 | 1.88 | 1.78
XKS | 0 | 399 | 0 | #DIV/0! |  | 2.07 | 1.97 | 1.93 | 1.91 | 1.93 | 1.92 | 1.92 | 1.92 | 1.93 | 1.91 | 1.91 | 1.9
XSN | 39.567 | 224.2 | 5 | 5.54 | Same | 1.62 | 1.61 | 1.58 | 1.64 | 1.7 | 1.78 | 1.76 | 1.76 | 1.79 | 1.8 | 1.82 | 1.82
XSY | 0 | 225.9 | 5 | #DIV/0! | Same | 1.72 | 1.69 | 1.61 | 1.61 | 1.61 | 1.59 | 1.58 | 1.58 | 1.66 | 1.6 | 1.6 | 1.6
Site Name | Current Usage (kW) | Building Load (kW) | Building Load Correction (do not modify) | PUE
XBL | 43.8725 | 94 | 0 | 2.1426
XCE | 9.374 | 124 | 0 | 13.2281
XCF | 39.6215 | 79 | 0 | 1.9939
XCN | #REF! |  | 0 | #REF!
TGW | 9.374 | 32 | 0 | 3.4137
XHN | #REF! |  | 0 | #REF!
XLR | #REF! |  | 0 | #REF!
XNE | #REF! | 149 | 0 | #REF!
XNY | #REF! |  | 0 | #REF!
XOD | #REF! | 78 | 0 | #REF!
XSD | #REF! | 174 | 0 | #REF!
TWN | 39.567 |  | 0 | 0
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Correction values RBS 5kW Normal Office 5kW Big office 40kW
Note on O8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Inconsistent readings
Note on O11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not reporting from 21/09-25/09
Note on G15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not reporting
Note on Y39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Cell equation is =(400*L4*1.73)/1000
Note on D40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Correction values RBS 5kW Normal Office 5kW Big office 40kW
Note on Y40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: cell equation is =(400*L5*1.73)/1000
Note on H41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Reading of 1.15. Didn’t record for a few days as BEMS systems was upgraded
Note on H43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual value of 0.52. Didn’t record for a few days as BEMS systems was upgraded
Note on I43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Didn't report for first 3 days of March due to BEMS upgrades
Note on I44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Didn't report for first 3 days of March due to BEMS upgrades
Note on L44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Actual fig of 0.97, BMS did not report 20-29 June
Note on D56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Correction values RBS 5kW Normal Office 5kW Big office 40kW
Note on B58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tech load from BMS= 294kW (add TSi kW fig). BMS PUE figs inc TSis from Jan onwards
Note on B59: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tech load from BMS= 231kW (add TSi kW fig). BMS PUE figs inc TSis from Jan onwards
Note on I62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is an approx fig as between 10-21 Mar the value was -0.04 resulting in an average of 0.93
Note on D72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Correction values RBS 5kW Normal Office 5kW Big office 40kW
Note on B74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tech load from BMS= 294kW (add TSi kW fig). BMS PUE figs inc TSis from Jan onwards
Note on B75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tech load from BMS= 231kW (add TSi kW fig). BMS PUE figs inc TSis from Jan onwards
Note on D96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Correction values RBS 5kW Normal Office 5kW Big office 40kW

## <90% plants and sites
NIR Date | Plant(s)/Site(s) | Request ref (VFPTSP no) | Comments
2022-07-12 | XLD & XMS | 22010 | Request for 5A AC rejected at XLD and XMS due to a no of DC plants being at >90%, XBE approved as decomms planned for PEFBE
2022-08-09 | XGL & XOM | 22013 | Request for M-PE expansion, plants not yet at <90%. Rejected due to prospective power requirement from NFV for next FY. Project to be asked for alternative site options
2022-12-02 | XMS and XEH | 22027 | XEH rejected due to power plants at capacity, XMS on hold pending investigation into why increase of approx 40A on PEDMS (may be due to possible PECMS controller failure) and possible power downs on PEDMS
2022-12-06 | XGR | 22028 | Request for x2 ISNG probes for 5G probing into empty Geoprobe cab 4 approved (10A per plant) as unlikely the RMS allocations of 206-230A on A,B and C are going to reach that
2022-12-15 | XMS | 22027 & 22010 | Request for VoiP Future probes and Secure Net blades approved as 7A allocation doesn't alter the 92% load (inc forecast and res'd figs, running load 83%) for PEDMS. NFV res'd load for PEDMS to be checked and DGWMS4 (on D and F) to be powered off in new year
2022-12-15 | XBE | 22007 | Request for NFV C7000 enclosures to be powered on approved on PEIBE (running load 78%, forecast & res'd takes it to 90%) as DSR to be powered off in new year (on E & I)
2023-09-12 | XGR | 23024 | Request for x11 RMS servers and switches, Allaister reported that Andy had approval from Lee which takes plants PECGR + PEDGR to 93%, site to 91% utilised
2023-09-28 | XBE and XMS | 23018 | Request for NFV TSR approved as will be gettting back approx 7kW per plant when Gen 9s powered down, overall approx 10kW per site increase
2023-10-10 | XBEand XMS | 23026 | Request for Fortinet servers approved as will be power returned at each site when TSRs installed and Gen 9s powered down
2023-10-12 | XEH | 23027 + 23028 | x4 ISNG probes required, apporved to go into Geoprobe Cab 5, remove 20A reserved NFV load from plants C,E and F, as it is for NFV probing. IPAR cab (AC powered) required for Security, approved due to large reserved load for NFV

## Inverter Numbering
Inverter system | Inverter Numbering | Comment
IC30aAN | Inv1
IC30aAN | Inv2
IC30aAN | Inv3
IC30aAN | Inv4
IC30aAN | Inv5
IC30aAN | Inv10
IC30aAN | Inv11
IC30aAN | Inv12
IC30aAN | Inv13
IC30aAN | Inv14
IC30aAN | Inv18
IC30aAN | Inv19
IC30aAN | Inv20
IC30aAN | Inv21
IC30aAN | Inv22
IC30aAN | Inv23
IC30aAN | Inv24
IC30aAN | Inv25
IC30aAN | Inv26
IC30bAN | Inv1
IC30bAN | Inv2
IC30bAN | Inv3
IC30bAN | Inv4
IC30bAN | Inv5
IC30bAN | Inv6
IC30bAN | Inv7
IC30bAN | Inv8
IC30bAN | Inv9
IC30bAN | Inv17
IC30bAN | Inv18
IC30bAN | Inv19
IC30bAN | Inv20
IC30bAN | Inv21
IC30bAN | Inv22
IC30bAN | Inv23
IC30bAN | Inv24
IC30bAN | Inv25
IC30bAN | Inv26
IC30aBE | Inv1
IC30aBE | Inv2
IC30aBE | Inv3
IC30aBE | Inv4
IC30aBE | Inv5
IC30aBE | Inv6
IC30aBE | Inv7
IC30aBE | Inv8
IC30aBE | Inv9 | DC switched off
IC30aBE | Inv10 | DC switched off
IC30aBE | Inv11
IC30aBE | Inv12
IC30aBE | Inv13
IC30aBE | Inv14
IC30aBE | Inv15
IC30aBE | Inv16
IC30aBE | Inv17
IC30aBE | Inv18
IC30aBE | Inv19 | DC switched off
IC30aBE | Inv20 | DC switched off
IC30aBE | Inv21
IC30aBE | Inv22
IC30aBE | Inv23
IC30aBE | Inv24
IC30aBE | Inv25
IC30aBE | Inv26
IC30aBE | Inv27
IC30aBE | Inv28
IC30aBE | Inv29
IC30aBE | Inv30
IC30bBE | Inv1
IC30bBE | Inv2
IC30bBE | Inv3
IC30bBE | Inv4
IC30bBE | Inv5
IC30bBE | Inv6
IC30bBE | Inv7
IC30bBE | Inv8
IC30bBE | Inv9
IC30bBE | Inv10
IC30bBE | Inv11
IC30bBE | Inv12
IC30bBE | Inv13
IC30bBE | Inv14
IC30bBE | Inv15
IC30bBE | Inv16
IC30bBE | Inv17
IC30bBE | Inv18
IC30bBE | Inv19
IC30bBE | Inv20
IC30bBE | Inv21
IC30bBE | Inv22
IC30bBE | Inv23
IC30bBE | Inv24
IC30bBE | Inv25
IC30bBE | Inv26
IC30bBE | Inv27 | DC switched off
IC30bBE | Inv28 | DC switched off
IC30bBE | Inv29 | DC switched off
IC30bBE | Inv30 | DC switched off
IC31aBE | Inv1
IC31aBE | Inv2
IC31aBE | Inv3
IC31aBE | Inv4
IC31aBE | Inv5
IC31aBE | Inv6
IC31aBE | Inv7
IC31aBE | Inv8
IC31aBE | Inv9 | Inverter off
IC31aBE | Inv10 | Inverter off
IC31aBE | Inv11
IC31aBE | Inv12
IC31aBE | Inv13
IC31aBE | Inv14
IC31aBE | Inv15
IC31aBE | Inv16
IC31aBE | Inv17
IC31aBE | Inv18
IC31aBE | Inv19
IC31aBE | Inv20
IC31aBE | Inv21
IC31aBE | Inv22
IC31aBE | Inv23
IC31aBE | Inv24
IC31aBE | Inv25
IC31aBE | Inv26
IC31aBE | Inv27
IC31aBE | Inv28
IC31aBE | Inv29 | Inverter off
IC31aBE | Inv30 | Inverter off
IC31bBE | Inv1
IC31bBE | Inv2
IC31bBE | Inv3
IC31bBE | Inv4
IC31bBE | Inv5
IC31bBE | Inv6
IC31bBE | Inv7
IC31bBE | Inv8
IC31bBE | Inv9
IC31bBE | Inv10
IC31bBE | Inv11
IC31bBE | Inv12
IC31bBE | Inv13
IC31bBE | Inv14
IC31bBE | Inv15
IC31bBE | Inv16
IC31bBE | Inv17
IC31bBE | Inv18
IC31bBE | Inv19
IC31bBE | Inv20
IC31bBE | Inv21
IC31bBE | Inv22
IC31bBE | Inv23
IC31bBE | Inv24
IC31bBE | Inv25
IC31bBE | Inv26
IC31bBE | Inv27 | Inverter off
IC31bBE | Inv28 | Inverter off
IC31bBE | Inv29 | Inverter off
IC31bBE | Inv30 | Inverter off
IC32aBE | Inv1
IC32aBE | Inv2
IC32aBE | Inv3
IC32aBE | Inv4
IC32aBE | Inv10
IC32aBE | Inv11
IC32aBE | Inv12
IC32aBE | Inv13
IC32aBE | Inv14
IC32aBE | Inv24
IC32aBE | Inv25
IC32aBE | Inv26
IC32bBE | Inv1
IC32bBE | Inv2
IC32bBE | Inv3
IC32bBE | Inv4
IC32bBE | Inv10
IC32bBE | Inv11
IC32bBE | Inv12
IC32bBE | Inv13
IC32bBE | Inv23
IC32bBE | Inv24
IC32bBE | Inv25
IC32bBE | Inv26
IC2BL | Inv1
IC2BL | Inv2
IC2BL | Inv3
IC2BL | Inv4
IC2BL | Inv5
IC2BL | Inv6
IC2CE | Inv1
IC2CE | Inv2
IC2CE | Inv3
IC2CE | Inv4
IC2CE | Inv5
IC2CE | Inv6
IC2CF | Inv1
IC2CF | Inv2
IC2CF | Inv3
IC2CF | Inv4
IC2CF | Inv5
IC2CF | Inv6
IC3CN | Inv1
IC3CN | Inv2
IC3CN | Inv3
IC3CN | Inv4
IC3CN | Inv5
IC3CN | Inv6
IC30aCY | Inv1
IC30aCY | Inv2
IC30aCY | Inv3
IC30aCY | Inv4
IC30aCY | Inv5
IC30aCY | Inv6
IC30aCY | Inv8
IC30aCY | Inv9
IC30aCY | Inv10
IC30aCY | Inv11
IC30aCY | Inv12
IC30aCY | Inv13
IC30bCY | Inv1
IC30bCY | Inv2
IC30bCY | Inv3
IC30bCY | Inv4
IC30bCY | Inv5
IC30bCY | Inv6
IC30bCY | Inv8
IC30bCY | Inv9
IC30bCY | Inv10
IC30bCY | Inv11
IC30bCY | Inv12
IC30bCY | Inv13
IC30aEH | Inv1
IC30aEH | Inv2
IC30aEH | Inv3
IC30aEH | Inv4
IC30aEH | Inv5
IC30aEH | Inv6
IC30aEH | Inv7
IC30aEH | Inv10
IC30aEH | Inv11
IC30aEH | Inv12
IC30aEH | Inv13
IC30aEH | Inv14
IC30aEH | Inv15
IC30aEH | Inv16
IC30aEH | Inv17
IC30aEH | Inv19
IC30aEH | Inv20
IC30aEH | Inv21
IC30aEH | Inv22
IC30aEH | Inv23
IC30aEH | Inv24
IC30aEH | Inv25
IC30bEH | Inv1
IC30bEH | Inv2
IC30bEH | Inv3
IC30bEH | Inv4
IC30bEH | Inv5
IC30bEH | Inv6
IC30bEH | Inv7
IC30bEH | Inv8
IC30bEH | Inv10
IC30bEH | Inv11
IC30bEH | Inv12
IC30bEH | Inv13
IC30bEH | Inv14
IC30bEH | Inv15
IC30bEH | Inv16
IC30bEH | Inv19
IC30bEH | Inv20
IC30bEH | Inv21
IC30bEH | Inv22
IC30bEH | Inv23
IC30bEH | Inv24
IC30bEH | Inv25
IC30aER | Inv1
IC30aER | Inv2
IC30aER | Inv3
IC30aER | Inv4
IC30aER | Inv5
IC30aER | Inv6
IC30aER | Inv8
IC30aER | Inv9
IC30aER | Inv10
IC30aER | Inv11
IC30aER | Inv12
IC30aER | Inv13
IC30bER | Inv1
IC30bER | Inv2
IC30bER | Inv3
IC30bER | Inv4
IC30bER | Inv5
IC30bER | Inv6
IC30bER | Inv8
IC30bER | Inv9
IC30bER | Inv10
IC30bER | Inv11
IC30bER | Inv12
IC30bER | Inv13
IC30aGL | Inv1
IC30aGL | Inv2
IC30aGL | Inv3
IC30aGL | Inv4
IC30aGL | Inv5
IC30aGL | Inv6
IC30aGL | Inv7
IC30aGL | Inv11
IC30aGL | Inv12
IC30aGL | Inv13
IC30aGL | Inv14
IC30aGL | Inv15
IC30aGL | Inv16
IC30aGL | Inv17
IC30aGL | Inv21
IC30aGL | Inv22
IC30aGL | Inv23
IC30aGL | Inv24
IC30aGL | Inv25
IC30aGL | Inv26
IC30aGL | Inv27
IC30bGL | Inv1
IC30bGL | Inv2
IC30bGL | Inv3
IC30bGL | Inv4
IC30bGL | Inv5
IC30bGL | Inv6
IC30bGL | Inv7
IC30bGL | Inv8
IC30bGL | Inv9
IC30bGL | Inv10
IC30bGL | Inv11
IC30bGL | Inv12
IC30bGL | Inv21
IC30bGL | Inv22
IC30bGL | Inv23
IC30bGL | Inv24
IC30bGL | Inv25
IC30bGL | Inv26
IC30bGL | Inv27
IC30bGL | Inv28
IC30bGL | Inv29
IC31aGL | Inv1
IC31aGL | Inv2
IC31aGL | Inv3
IC31aGL | Inv4
IC31aGL | Inv5
IC31aGL | Inv6
IC31aGL | Inv7
IC31aGL | Inv11
IC31aGL | Inv12
IC31aGL | Inv13
IC31aGL | Inv14
IC31aGL | Inv15
IC31aGL | Inv16
IC31aGL | Inv17
IC31aGL | Inv21
IC31aGL | Inv22
IC31aGL | Inv23
IC31aGL | Inv24
IC31aGL | Inv25
IC31aGL | Inv26
IC31aGL | Inv27
IC31bGL | Inv1
IC31bGL | Inv2
IC31bGL | Inv3
IC31bGL | Inv4
IC31bGL | Inv5
IC31bGL | Inv6
IC31bGL | Inv7
IC31bGL | Inv8
IC31bGL | Inv9
IC31bGL | Inv10
IC31bGL | Inv11
IC31bGL | Inv12
IC31bGL | Inv13
IC31bGL | Inv14
IC31bGL | Inv15
IC31bGL | Inv21
IC31bGL | Inv22
IC31bGL | Inv23
IC31bGL | Inv24
IC31bGL | Inv25
IC31bGL | Inv26
IC30aGR | Inv1
IC30aGR | Inv2
IC30aGR | Inv3
IC30aGR | Inv4
IC30aGR | Inv5
IC30aGR | Inv6
IC30aGR | Inv7
IC30aGR | Inv8
IC30aGR | Inv9
IC30aGR | Inv10
IC30aGR | Inv11
IC30aGR | Inv12
IC30aGR | Inv13
IC30aGR | Inv14
IC30bGR | Inv1
IC30bGR | Inv2
IC30bGR | Inv3
IC30bGR | Inv4
IC30bGR | Inv5
IC30bGR | Inv6
IC30bGR | Inv7
IC30bGR | Inv8
IC30bGR | Inv9
IC30bGR | Inv10
IC30bGR | Inv11
IC30bGR | Inv12
IC30bGR | Inv13
IC30bGR | Inv14
IC30aKS | Inv1
IC30aKS | Inv2
IC30aKS | Inv3
IC30aKS | Inv4
IC30aKS | Inv5
IC30aKS | Inv6
IC30aKS | Inv7
IC30aKS | Inv8
IC30aKS | Inv9
IC30aKS | Inv10
IC30aKS | Inv11
IC30aKS | Inv12
IC30aKS | Inv13
IC30aKS | Inv14
IC30aKS | Inv15
IC30aKS | Inv16
IC30aKS | Inv17
IC30aKS | Inv18
IC30aKS | Inv19
IC30aKS | Inv20
IC30aKS | Inv21
IC30aKS | Inv22
IC30aKS | Inv23
IC30aKS | Inv24
IC30bKS | Inv1
IC30bKS | Inv2
IC30bKS | Inv3
IC30bKS | Inv4
IC30bKS | Inv5
IC30bKS | Inv6
IC30bKS | Inv7
IC30bKS | Inv8
IC30bKS | Inv9
IC30bKS | Inv10
IC30bKS | Inv11
IC30bKS | Inv12
IC30bKS | Inv13
IC30bKS | Inv14
IC30bKS | Inv15
IC30bKS | Inv16
IC30bKS | Inv17
IC30bKS | Inv18
IC30bKS | Inv19
IC30bKS | Inv20
IC30bKS | Inv21
IC30bKS | Inv22
IC30bKS | Inv23
IC30bKS | Inv24
IC30aLD | Inv1
IC30aLD | Inv2
IC30aLD | Inv3
IC30aLD | Inv4
IC30aLD | Inv5
IC30aLD | Inv6
IC30aLD | Inv7
IC30aLD | Inv8
IC30aLD | Inv9
IC30aLD | Inv11
IC30aLD | Inv12
IC30aLD | Inv13
IC30aLD | Inv14
IC30aLD | Inv15
IC30aLD | Inv16
IC30aLD | Inv17
IC30aLD | Inv18
IC30aLD | Inv19
IC30aLD | Inv21
IC30aLD | Inv22
IC30aLD | Inv23
IC30aLD | Inv24
IC30aLD | Inv25
IC30aLD | Inv26
IC30aLD | Inv27
IC30aLD | Inv28
IC30bLD | Inv1
IC30bLD | Inv2
IC30bLD | Inv3
IC30bLD | Inv4
IC30bLD | Inv5
IC30bLD | Inv6
IC30bLD | Inv7
IC30bLD | Inv8
IC30bLD | Inv9
IC30bLD | Inv11
IC30bLD | Inv12
IC30bLD | Inv13
IC30bLD | Inv14
IC30bLD | Inv15
IC30bLD | Inv16
IC30bLD | Inv17
IC30bLD | Inv18
IC30bLD | Inv21
IC30bLD | Inv22
IC30bLD | Inv23
IC30bLD | Inv24
IC30bLD | Inv25
IC30bLD | Inv26
IC30bLD | Inv27
IC30bLD | Inv28
IC30bLD | Inv29
IC3LR | Inv1
IC3LR | Inv2
IC3LR | Inv3
IC3LR | Inv4
IC3LR | Inv5
IC3LR | Inv6
IC20aMS | Inv1
IC20aMS | Inv2
IC20aMS | Inv3
IC20aMS | Inv4
IC20aMS | Inv5
IC20aMS | Inv6
IC20aMS | Inv7
IC20aMS | Inv11
IC20aMS | Inv12
IC20aMS | Inv13
IC20aMS | Inv14
IC20aMS | Inv15
IC20aMS | Inv16
IC20aMS | Inv17
IC20aMS | Inv21
IC20aMS | Inv22
IC20aMS | Inv23
IC20aMS | Inv24
IC20aMS | Inv25
IC20aMS | Inv26
IC20aMS | Inv27
IC20bMS | Inv1
IC20bMS | Inv2
IC20bMS | Inv3
IC20bMS | Inv4
IC20bMS | Inv5
IC20bMS | Inv6
IC20bMS | Inv7
IC20bMS | Inv11
IC20bMS | Inv12
IC20bMS | Inv13
IC20bMS | Inv14
IC20bMS | Inv15
IC20bMS | Inv16
IC20bMS | Inv17
IC20bMS | Inv21
IC20bMS | Inv22
IC20bMS | Inv23
IC20bMS | Inv24
IC20bMS | Inv25
IC20bMS | Inv26
IC20bMS | Inv27
IC30aMS | Inv1
IC30aMS | Inv2
IC30aMS | Inv3
IC30aMS | Inv4
IC30aMS | Inv5
IC30aMS | Inv6
IC30aMS | Inv7
IC30aMS | Inv11
IC30aMS | Inv12 | DC Connected by not used
IC30aMS | Inv13
IC30aMS | Inv14
IC30aMS | Inv15
IC30aMS | Inv16
IC30aMS | Inv17 | DC Connected by not used
IC30aMS | Inv21
IC30aMS | Inv22
IC30aMS | Inv23
IC30aMS | Inv24
IC30aMS | Inv25
IC30aMS | Inv26
IC30aMS | Inv27
IC30aMS | Inv28 | DC Connected by not used
IC30bMS | Inv1
IC30bMS | Inv2
IC30bMS | Inv3
IC30bMS | Inv4
IC30bMS | Inv5
IC30bMS | Inv6
IC30bMS | Inv7
IC30bMS | Inv11
IC30bMS | Inv12
IC30bMS | Inv13
IC30bMS | Inv14
IC30bMS | Inv15
IC30bMS | Inv16
IC30bMS | Inv17 | DC Connected by not used
IC30bMS | Inv21
IC30bMS | Inv22
IC30bMS | Inv23
IC30bMS | Inv24
IC30bMS | Inv25
IC30bMS | Inv26
IC30bMS | Inv27 | DC Connected by not used
IC30bMS | Inv28 | DC Connected by not used
IC31aMS | Inv1
IC31aMS | Inv2
IC31aMS | Inv3
IC31aMS | Inv4
IC31aMS | Inv5
IC31aMS | Inv6
IC31aMS | Inv7
IC31aMS | Inv8
IC31aMS | Inv11
IC31aMS | Inv12
IC31aMS | Inv13
IC31aMS | Inv14
IC31aMS | Inv15
IC31aMS | Inv16
IC31aMS | Inv17
IC31aMS | Inv18
IC31aMS | Inv21
IC31aMS | Inv22
IC31aMS | Inv23
IC31aMS | Inv24
IC31aMS | Inv25
IC31aMS | Inv26
IC31aMS | Inv27
IC31aMS | Inv28
IC31aMS | Inv29
IC31bMS | Inv1
IC31bMS | Inv2
IC31bMS | Inv3
IC31bMS | Inv4
IC31bMS | Inv5
IC31bMS | Inv6
IC31bMS | Inv7
IC31bMS | Inv8
IC31bMS | Inv9
IC31bMS | Inv10
IC31bMS | Inv11
IC31bMS | Inv12
IC31bMS | Inv13
IC31bMS | Inv14
IC31bMS | Inv15
IC31bMS | Inv16
IC31bMS | Inv17
IC31bMS | Inv18
IC31bMS | Inv21
IC31bMS | Inv22
IC31bMS | Inv23
IC31bMS | Inv24
IC31bMS | Inv25
IC31bMS | Inv26
IC31bMS | Inv27
IC3NE | Inv1
IC3NE | Inv2
IC3NE | Inv3
IC3NE | Inv4
IC3NE | Inv5
IC3NE | Inv6
IC4NY | Inv1
IC4NY | Inv2
IC4NY | Inv3
IC4NY | Inv4
IC4NY | Inv5
IC4NY | Inv6
IC4NY | Inv7
IC4NY | Inv8
IC4NY | Inv8 | DC switched off
IC4NY | Inv9 | DC switched off
IC4NY | Inv11 | DC switched off
IC4NY | Inv12 | DC switched off
IC2OD | Inv1
IC2OD | Inv2
IC2OD | Inv3
IC2OD | Inv4
IC2OD | Inv5
IC2OD | Inv6
IC30aOM | Inv1
IC30aOM | Inv2
IC30aOM | Inv3
IC30aOM | Inv4
IC30aOM | Inv5
IC30aOM | Inv6
IC30aOM | Inv7
IC30aOM | Inv8
IC30aOM | Inv9
IC30aOM | Inv10
IC30aOM | Inv11
IC30aOM | Inv12
IC30aOM | Inv13
IC30aOM | Inv14
IC30aOM | Inv15
IC30aOM | Inv16
IC30aOM | Inv17
IC30aOM | Inv18
IC30aOM | Inv19
IC30aOM | Inv20
IC30aOM | Inv21
IC30aOM | Inv22
IC30aOM | Inv23
IC30aOM | Inv24
IC30aOM | Inv25
IC30aOM | Inv26
IC30bOM | Inv1
IC30bOM | Inv2
IC30bOM | Inv3
IC30bOM | Inv4
IC30bOM | Inv5
IC30bOM | Inv6
IC30bOM | Inv7
IC30bOM | Inv8
IC30bOM | Inv9
IC30bOM | Inv10
IC30bOM | Inv11
IC30bOM | Inv12
IC30bOM | Inv13
IC30bOM | Inv14
IC30bOM | Inv15
IC30bOM | Inv16
IC30bOM | Inv17
IC30bOM | Inv18
IC30bOM | Inv19
IC30bOM | Inv20
IC30bOM | Inv21
IC30bOM | Inv22
IC30bOM | Inv23
IC30bOM | Inv24
IC30bOM | Inv25
IC30bOM | Inv26
IC30aRM | Inv1
IC30aRM | Inv2
IC30aRM | Inv3
IC30aRM | Inv4
IC30aRM | Inv5
IC30aRM | Inv6
IC30aRM | Inv8
IC30aRM | Inv9
IC30aRM | Inv10
IC30aRM | Inv11
IC30aRM | Inv12
IC30aRM | Inv13
IC30bRM | Inv1
IC30bRM | Inv2
IC30bRM | Inv3
IC30bRM | Inv4
IC30bRM | Inv5
IC30bRM | Inv6
IC30bRM | Inv8
IC30bRM | Inv9
IC30bRM | Inv10
IC30bRM | Inv11
IC30bRM | Inv12
IC30bRM | Inv13
IC3SD | Inv1
IC3SD | Inv2
IC3SD | Inv3
IC3SD | Inv4
IC3SD | Inv5
IC3SD | Inv6
IC30aSN | Inv1
IC30aSN | Inv2
IC30aSN | Inv3
IC30aSN | Inv4
IC30aSN | Inv5
IC30aSN | Inv6
IC30aSN | Inv8
IC30aSN | Inv9
IC30aSN | Inv10
IC30aSN | Inv11
IC30aSN | Inv12
IC30aSN | Inv13
IC30bSN | Inv1
IC30bSN | Inv2
IC30bSN | Inv3
IC30bSN | Inv4
IC30bSN | Inv5
IC30bSN | Inv6
IC30bSN | Inv8
IC30bSN | Inv9
IC30bSN | Inv10
IC30bSN | Inv11
IC30bSN | Inv12
IC30bSN | Inv13
IC30aSY | Inv1
IC30aSY | Inv2
IC30aSY | Inv3
IC30aSY | Inv4
IC30aSY | Inv5
IC30aSY | Inv6
IC30aSY | Inv8
IC30aSY | Inv9
IC30aSY | Inv10
IC30aSY | Inv11
IC30aSY | Inv12
IC30aSY | Inv13
IC30bSY | Inv1
IC30bSY | Inv2
IC30bSY | Inv3
IC30bSY | Inv4
IC30bSY | Inv5
IC30bSY | Inv6
IC30bSY | Inv8
IC30bSY | Inv9
IC30bSY | Inv10
IC30bSY | Inv11
IC30bSY | Inv12
IC30bSY | Inv13
IC1GW | Inv1
IC1GW | Inv2 | Distributed DC feed
IC1GW | Inv3 | Distributed DC feed
GCRMTX-INV02a | Inv1
GCRMTX-INV02a | Inv2
GCRMTX-INV02a | Inv3
GCRMTX-INV02a | Inv4
GCRMTX-INV02a | Inv5
GCRMTX-INV02a | Inv6
GCRMTX-INV02a | Inv7
GCRMTX-INV02a | Inv8
GCRMTX-INV02a | Inv9
GCRMTX-INV02a | Inv10
GCRMTX-INV02a | Inv11
GCRMTX-INV02a | Inv12
GCRMTX-INV02a | Inv13
GCRMTX-INV02a | Inv14
GCRMTX-INV02a | Inv15 | DC switched off
GCRMTX-INV02a | Inv16 | DC switched off
GCRMTX-INV02b | Inv1
GCRMTX-INV02b | Inv2
GCRMTX-INV02b | Inv3
GCRMTX-INV02b | Inv4
GCRMTX-INV02b | Inv5
GCRMTX-INV02b | Inv6
GCRMTX-INV02b | Inv7
GCRMTX-INV02b | Inv8
GCRMTX-INV02b | Inv9
GCRMTX-INV02b | Inv10
GCRMTX-INV02b | Inv11
GCRMTX-INV02b | Inv12
GCRMTX-INV02b | Inv13
GCRMTX-INV02b | Inv14
GCRMTX-INV02b | Inv15 | DC switched off
GCRMTX-INV02b | Inv16 | DC switched off
IC3WN | Inv1
IC3WN | Inv2
IC3WN | Inv3