## Suite Line Capacity
Report generated for: | Room EVMN01 on Floor Ground Floor in Site EVESHAM
| Quantity | % of all area | Area
Total free sections: | 17/36 | 51 % | 4.428 m²
Total occupied sections: | 19/36 | 49 % | 4.313 m²
Total reserved sections: | 0/36 | 0 % | 0.000 m²
Total Lines Capability |  |  | 8.740 m²
Total Location Capability |  |  | 59.400 m²
Total Location Free Area |  |  | 55.088 m²
Total Location Occupied Area |  |  | 4.313 m²
Location | Power Consumption | Cooling Capability | Utilized Cooling Capability [%] | Suite Line | [5 empty] | Rack description | Free rack units |  |  | Max free space in rack units
Location | Power Consumption | Cooling Capability | Utilized Cooling Capability [%] | Suite Line Name | Number of Sections |  | Number of Sections | % of all area | Area | Rack description | front | back | straight through | front | back | straight through
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | A | 5 | Free | 2 | 50 % | 0.600 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | A | 5 | Occupied | 3 | 50 % | 0.600 m² | Rack AB3, Floor Position = A3 | 36 | 42 | 36 | 35 | 42 | 35
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | A | 5 | Occupied | 3 | 50 % | 0.600 m² | Rack B02, Floor Position = A2 | 20 | 30 | 16 | 10 | 23 | 10
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | A | 5 | Occupied | 3 | 50 % | 0.600 m² | Rack A1, Floor Position = A1 | 43 | 31 | 29 | 38 | 27 | 20
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | A | 5 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | B | 5 | Free | 2 | 40 % | 0.480 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | B | 5 | Occupied | 3 | 60 % | 0.720 m² | Rack AB3, Floor Position = A3 | 36 | 42 | 36 | 35 | 42 | 35
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | B | 5 | Occupied | 3 | 60 % | 0.720 m² | Rack B02, Floor Position = A2 | 20 | 30 | 16 | 10 | 23 | 10
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | B | 5 | Occupied | 3 | 60 % | 0.720 m² | Rack A1, Floor Position = A1 | 43 | 31 | 29 | 38 | 27 | 20
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | B | 5 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Free | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Occupied | 4 | 100 % | 0.900 m² | ODF CODF C5, Floor Position = C5 | 39 | 47 | 39 | 27 | 47 | 27
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Occupied | 4 | 100 % | 0.900 m² | ODF C3, Floor Position = C3 | 44 | 46 | 44 | 23 | 46 | 23
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Occupied | 4 | 100 % | 0.900 m² | Rack C1, Floor Position = C1 | 8 | 44 | 8 | 2 | 44 | 2
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Occupied | 4 | 100 % | 0.900 m² | Rack C2, Floor Position = C2 | 22 | 44 | 22 | 20 | 44 | 20
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | C | 4 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | D | 4 | Free | 3 | 70 % | 0.630 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | D | 4 | Occupied | 1 | 30 % | 0.270 m² | ODF D5, Floor Position = D5 | 41 | 46 | 41 | 41 | 46 | 41
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | D | 4 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | E | 4 | Free | 3 | 75 % | 0.788 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | E | 4 | Occupied | 1 | 25 % | 0.263 m² | Rack E01, Floor Position = E1 | 35 | 45 | 35 | 27 | 45 | 27
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | E | 4 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | F | 5 | Free | 5 | 100 % | 1.050 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | F | 5 | Occupied | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | F | 5 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | G | 4 | Free | 1 | 40 % | 0.360 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | G | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack G4, Floor Position = G4 | 5 | 47 | 5 | 5 | 47 | 5
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | G | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack EVMN01;DC SYS01, Floor Position = G02 | 19 | 46 | 19 | 18 | 25 | 18
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | G | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack G1, Floor Position = G1 | 42 | 42 | 42 | 42 | 42 | 42
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | G | 4 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | H | 4 | Free | 1 | 40 % | 0.360 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | H | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack G4, Floor Position = G4 | 5 | 47 | 5 | 5 | 47 | 5
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | H | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack G1, Floor Position = G1 | 42 | 42 | 42 | 42 | 42 | 42
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | H | 4 | Occupied | 3 | 60 % | 0.540 m² | Rack EVMN01;DC SYS01, Floor Position = G02 | 19 | 46 | 19 | 18 | 25 | 18
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | H | 4 | Reserved | 0 | 0 % | 0.000 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | J | 1 | Free | 0 | 25 % | 0.160 m²
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | J | 1 | Occupied | 1 | 75 % | 0.480 m² | Rack J0, Floor Position = J00 | 7 | 21 | 7 | 6 | 21 | 6
Room EVMN01 on Floor Ground Floor in Site EVESHAM | 14295.50 W | 11250.00 W | 127 % | J | 1 | Reserved | 0 | 0 % | 0.000 m²