## Suite Line Capacity
Report generated for: | Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM
| Quantity | % of all area | Area
Total free sections: | 2/36 | 23 % | 2.016 m²
Total occupied sections: | 34/36 | 77 % | 6.839 m²
Total reserved sections: | 0/36 | 0 % | 0.000 m²
Total Lines Capability |  |  | 8.855 m²
Total Location Capability |  |  | 28.000 m²
Total Location Free Area |  |  | 21.161 m²
Total Location Occupied Area |  |  | 6.839 m²
Location | Power Consumption | Cooling Capability | Utilized Cooling Capability [%] | Suite Line | [5 empty] | Rack description | Free rack units |  |  | Max free space in rack units
Location | Power Consumption | Cooling Capability | Utilized Cooling Capability [%] | Suite Line Name | Number of Sections |  | Number of Sections | % of all area | Area | Rack description | front | back | straight through | front | back | straight through
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Free | 0 | 33 % | 1.080 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A5, Floor Position = A05 | 23 | 47 | 23 | 21 | 47 | 21
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A6, Floor Position = A06 | 47 | 47 | 47 | 47 | 47 | 47
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A7, Floor Position = A07 | 42 | 42 | 42 | 42 | 42 | 42
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack INVTL1;DC SYS01, Floor Position = A08 | 20 | 46 | 20 | 19 | 25 | 19
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A3, Floor Position = A03 | 11 | 47 | 11 | 4 | 47 | 4
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A4, Floor Position = A04 | 23 | 47 | 23 | 23 | 47 | 23
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A0, Floor Position = A00 | 5 | 47 | 5 | 5 | 47 | 5
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A1, Floor Position = A01 | 8 | 47 | 8 | 4 | 47 | 4
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Occupied | 9 | 67 % | 2.160 m² | Rack A2, Floor Position = A02 | 11 | 47 | 11 | 4 | 47 | 4
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | A | 9 | Reserved | 0 | 0 % | 0.000 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Free | 1 | 10 % | 0.164 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B8, Floor Position = B8 | 16 | 47 | 16 | 8 | 47 | 8
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B6, Floor Position = B6 | 6 | 47 | 6 | 5 | 47 | 5
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B7, Floor Position = B7 | 36 | 47 | 36 | 16 | 47 | 16
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B5, Floor Position = B5 | 7 | 39 | 7 | 6 | 39 | 6
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B1, Floor Position = B1 | 19 | 39 | 19 | 8 | 39 | 8
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B3, Floor Position = B3 | 47 | 47 | 47 | 47 | 47 | 47
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B4, Floor Position = B4 | 34 | 29 | 20 | 20 | 13 | 7
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Occupied | 8 | 90 % | 1.500 m² | Rack B2, Floor Position = B2 | 21 | 47 | 21 | 13 | 47 | 13
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | B | 9 | Reserved | 0 | 0 % | 0.000 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Free | 0 | 7 % | 0.120 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack C8, Floor Position = C8 | 7 | 47 | 7 | 3 | 47 | 3
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack C9, Floor Position = C09 | 5 | 47 | 5 | 5 | 47 | 5
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B6, Floor Position = B6 | 6 | 47 | 6 | 5 | 47 | 5
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B7, Floor Position = B7 | 36 | 47 | 36 | 16 | 47 | 16
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B5, Floor Position = B5 | 7 | 39 | 7 | 6 | 39 | 6
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B1, Floor Position = B1 | 19 | 39 | 19 | 8 | 39 | 8
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B3, Floor Position = B3 | 47 | 47 | 47 | 47 | 47 | 47
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B4, Floor Position = B4 | 34 | 29 | 20 | 20 | 13 | 7
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Occupied | 9 | 93 % | 1.544 m² | Rack B2, Floor Position = B2 | 21 | 47 | 21 | 13 | 47 | 13
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | C | 9 | Reserved | 0 | 0 % | 0.000 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Free | 1 | 29 % | 0.652 m²
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D4, Floor Position = D4 | 18 | 47 | 18 | 8 | 47 | 8
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D2, Floor Position = D2 | 36 | 42 | 36 | 36 | 42 | 36
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D1, Floor Position = D1 | 31 | 47 | 31 | 30 | 47 | 30
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D3, Floor Position = D3 | 3 | 47 | 3 | 1 | 47 | 1
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D0, Floor Position = D0 | 47 | 47 | 47 | 47 | 47 | 47
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | ODF D8, Floor Position = D8 | 7 | 42 | 7 | 4 | 42 | 4
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | Rack D5, Floor Position = D5 | 10 | 47 | 10 | 4 | 47 | 4
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Occupied | 8 | 71 % | 1.635 m² | ODF D7, Floor Position = D7 | 3 | 47 | 3 | 3 | 47 | 3
Room INVTL1 on Floor Ground Floor in Site LONGMAN EAM | 33730.00 W | 10500.00 W | 321 % | D | 9 | Reserved | 0 | 0 % | 0.000 m²